## Check Monitoring Results
Potable Water Mains Supply - Check Monitoring Analytical Results
Samples from the potable water distribution network are collected and analysed by AquaGib on a weekly basis.
Standards are in accordance with the Public Health Water Rules 1994, which incoporate the requirements set by the European Directive of Drinking Water 98/83/EC
Note 1: Acceptable to consumers and no abnormal change
Sample Location | Date of Collection of Sample | Analysis Reference Number | Parameter | Ammonia | Appearance | Chloride | Electrical Conductivity | Odour | pH | Taste | Turbidity | Coliform | Esherichia Coli
|  |  | Units | mg/l NH4 | Qualitative | mg/l Cl | μS/cm | Qualitative | pH value | Qualitative | NTU | no/100ml | no/100ml
|  |  | Standard | 0.5 | Note 1 | 250 | 2500 | Note 1 | 6.5 to 9.5 | Note 1 | Note 1 | 0 | 0
L/Level / John McIntosh Square | 2006-07-06 | J1 |  | nil | clear | 158 | 619 | none | 7.99 | none | 0.36 | 0 | 0
Reclamation / Varyl Begg | 2006-07-06 | J2 |  | nil | clear | 166 | 636 | none | 8.27 | none | 0.2 | 0 | 0
L/Level / ICC | 2006-07-11 | J4 |  | nil | clear | 159 | 627 | none | 8.14 | none | 0.34 | 0 | 0
S/District / Rosia Dale | 2006-07-11 | J5 |  | nil | clear | 164 | 631 | none | 8.1 | none | 1.39 | 0 | 0
L/Level / Governor's Parade | 2006-07-20 | J6 |  | nil | clear | 163 | 649 | none | 8.16 | none | 0.36 | 0 | 0
High Level / Willis's Rd | 2006-07-20 | J7 |  | nil | clear | 155 | 640 | none | 8.34 | none | 0.41 | 0 | 0
L/Level / Governor's Parade | 2006-07-28 | J8 |  | nil | clear | 160 | 631 | none | 8.26 | none | 0.35 | 0 | 0
Waterport / Desal plant canteen | 2006-07-28 | J9 |  | nil | clear | 140 | 643 | none | 8.19 | none | 0.22 | 0 | 0
L/Level / Town Range | 2006-08-04 | A1 |  | nil | clear | 149 | 626 | none | 8.05 | none | 0.77 | 0 | 0
N/Front/ Both Worlds | 2006-08-04 | A2 |  | 0.005 | clear | 155 | 708 | none | 7.85 | none | 0.16 | 0 | 0
L/Level / Police Station | 2006-08-08 | A3 |  | nil | clear | 149 | 648 | none | 8.02 | none | 1.26 | 0 | 0
Reclamation/ varyl begg | 2006-08-08 | A4 |  | nil | clear | 152 | 645 | none | 7.86 | none | 0.48 | 0 | 0
L/Level / Eliots Hotel | 2006-08-15 | A5 |  | nil | clear | 157 | 639 | none | 8.01 | none | 0.88 | 0 | 0
Waterport/ Aqua gib tap | 2006-08-15 | A6 |  | nil | clear | 152 | 641 | none | 8.09 | none | 0.88 | 0 | 0
L/Level / John Mcintosh Hall | 2006-08-21 | A7 |  | nil | clear | 160 | 664 | none | 8.01 | none | 1.72 | 0 | 0
S/District/ Rosia dale | 2006-08-21 | A8 |  | 0.04 | clear | 174 | 652 | none | 8.18 | none | 1.09 | 0 | 0
L/Level / ICC | 2006-08-29 | A9 |  | 0.02 | clear | 153 | 596 | none | 8.28 | none | 1.1 | 0 | 0
H/Level / Carters Willis,s Rd | 2006-08-29 | A10 |  | 0.02 | clear | 176 | 635 | none | 8.07 | none | 0.36 | 0 | 0
L/Level / Eliots Hotel sq | 2006-09-07 | S1 |  | nil | clear | 164 | 647 | none | 8.21 | none | 0.61 | 0 | 0
N/Front/ SANDY BAY | 2006-09-07 | S2 |  | nil | clear | 129 | 566 | none | 8.16 | none | 0.13 | 0 | 0
L/Level / McKintosh Hall | 2006-09-13 | S3 |  | nil | clear | 168 | 660 | none | 8.11 | none | 0.32 | 0 | 0
Reclamation/ Toyota garage | 2006-09-13 | S4 |  | nil | clear | 161 | 731 | none | 8.27 | none | 0.18 | 0 | 0
L/Level / ICC | 2006-09-19 | S7 |  | 0.001 | clear | 174 | 699 | none | 8.16 | none | 0.67 | 0 | 0
Waterport/ Tourist Board garage | 2006-09-19 | S6 |  | nil | clear | 175 | 657 | none | 8.05 | none | 0.57 | 0 | 0
L/Level / Mckintosh Hall | 2006-09-27 | S7 |  | nil | clear | 177 | 685 | none | 8.11 | none | 0.33 | 0 | 0
S/District/ St Joseph School | 2006-09-27 | S8 |  | nil | clear | 173 | 697 | none | 7.86 | none | 0.27 | 0 | 0
L/Level / I.C.C | 2006-10-03 | O1 |  | nil | clear | 177 | 684 | none | 8.1 | none | 0.69 | 0 | 0
H/Level / Sacred Heart School | 2006-10-03 | O2 |  | nil | clear | 176 | 725 | none | 8.28 | none | 0.25 | 0 | 0
L/Level / Elliots Hotel | 2006-10-12 | O3 |  | nil | clear | 180 | 707 | none | 7.94 | none | 0.11 | 0 | 0
North Front / Both Worlds | 2006-10-12 | O4 |  | nil | clear | 184 | 791 | none | 7.81 | none | 0.56 | 0 | 0
L/Level / 106 Irish Town | 2006-10-19 | O5 |  | nil | clear | 180 | 658 | none | 7.99 | none | 0.38 | 0 | 0
Reclamation / Gov Med School | 2006-10-19 | O6 |  | nil | clear | 165 | 637 | none | 8.08 | none | 0.35 | 0 | 0
L/Level / No4 Governer's Parade | 2006-10-25 | O7 |  | nil | clear | 176 | 638 | none | 7.88 | none | 0.36 | 0 | 0
S/District / Tiny Tots Nursery | 2006-10-25 | O8 |  | nil | clear | 147 | 580 | none | 7.94 | none | 0.27 | 0 | 0
L/Level / Shell House Line wall Rd | 2006-11-02 | N1 |  | nil | clear | 174 | 633 | none | 7.54 | none | 0.29 | 0 | 0
H/Level / Lime Kiln Steps | 2006-11-02 | N2 |  | nil | clear | 187 | 748 | none | 8.12 | none | 0.31 | 0 | 0
L/Level / Parcel post Depot | 2006-11-07 | N3 |  | nil | clear | 172 | 641 | none | 7.93 | none | 0.75 | 0 | 0
North Front / Bassadone Motors | 2006-11-07 | N4 |  | nil | clear | 159 | 636 | none | 8.14 | none | 0.76 | 0 | 0
L/Level/Gibraltar Chronicle | 2006-11-16 | N5 |  | nil | clear | 151 | 625 | none | 8.01 | none | 1.95 | 0 | 0
Reclamation/Safeway Supermarket | 2006-11-16 | N6 |  | nil | clear | 166 | 647 | none | 8.05 | none | 0.35 | 0 | 0
L/Level /14 Town Range | 2006-11-20 | N7 |  | nil | clear | 167 | 626 | none | 8.1 | none | 0.96 | 0 | 0
Waterport/ Aquagib Distiller Canteen | 2006-11-20 | N8 |  | nil | clear | 160 | 607 | none | 8.16 | none | 1.07 | 0 | 0
L/Level /I.C.C | 2006-11-28 | N9 |  | nil | clear | 153 | 579 | none | 8.14 | none | 0.27 | 0 | 0
South District / Alameda Estate | 2006-11-28 | N10 |  | nil | clear | 161 | 619 | none | 8.09 | none | 0.81 | 0 | 0
High Level / St Bernard's F School | 2006-12-08 | D1 |  | nil | clear | 159 | 610 | none | 8.18 | none | 0.36 | 0 | 0
Low Level / Gibraltar College | 2006-12-08 | D2 |  | nil | clear | 157 | 615 | none | 8.35 | none | 0.23 | 0 | 0
North Front / Laguna Estate | 2006-12-15 | D3 |  | nil | clear | 149 | 597 | none | 8.02 | none | 0.45 | 0 | 0
Low Level / St Mary's F School | 2006-12-15 | D4 |  | nil | clear | 153 | 628 | none | 7.97 | none | 1.02 | 0 | 0
Low Level / Town Range | 2006-12-18 | D5 |  | nil | clear | 154 | 606 | none | 8.21 | none | 0.41 | 0 | 0
Reclamation / St Bernard's Hosp | 2006-12-18 | D6 |  | nil | clear | 156 | 620 | none | 8.27 | none | 0.11 | 0 | 0
Low Level / Central Police Station | 2006-12-27 | D7 |  | nil | clear | 136 | 579 | none | 8.33 | none | 0.41 | 0 | 0
Waterport/Gib Electrical Power Stn | 2006-12-27 | D8 |  | nil | clear | 143 | 577 | none | 8.27 | none | 0.32 | 0 | 0
Low Level / Mini Market | 2007-01-04 | J1-1 |  | 0.02 | clear | 158 | 596 | none | 7.83 | none | 0.56 | 0 | 0
High Level / Flat Bastion Road | 2007-01-04 | J1-2 |  | 0.024 | clear | 134 | 548 | none | 8.34 | none | 0.9 | 0 | 0
Low Level / Social Security | 2007-01-08 | J1-3 |  | nil | clear | 152 | 590 | none | 7.65 | none | 0.34 | 0 | 0
South District / The New Harbours | 2007-01-08 | J1-4 |  | nil | clear | 125 | 518 | none | 7.68 | none | 0.17 | 0 | 0
Low/Level / Parcel Post | 2007-01-16 | J1-5 |  | nil | clear | 110 | 539 | none | 7.97 | none | 0.21 | 0 | 0
North Front / Bassadone Motors | 2007-01-16 | J1-6 |  | nil | clear | 110 | 458 | none | 8.06 | none | 1.16 | 0 | 0
Low Level / Shell Line Wall Rd | 2007-01-21 | J1-7 |  | nil | clear | 133 | 532 | none | 7.71 | none | 0.28 | 0 | 0
Waterport / Helm Marine North Mole | 2007-01-21 | J1-8 |  | nil | clear | 142 | 565 | none | 8.01 | none | 0.67 | 0 | 0
Low Level /I.C.C | 2007-01-30 | J1-9 |  | nil | clear | 130 | 585 | none | 7.64 | none | 0.48 | 0 | 0
Reclamation / Safeway Supermarket | 2007-01-30 | J1-10 |  | nil | clear | 163 | 643 | none | 7.74 | none | 0.61 | 0 | 0
Low Level / Gibraltar Chronicle | 2007-02-07 | F1-1 |  | nil | clear | 147 | 619 | none | 7.84 | none | 0.14 | 0 | 0
High Level / Lime Kiln Steps | 2007-02-07 | F1-2 |  | nil | clear | 147 | 610 | none | 8.19 | none | 0.44 | 0 | 0
South Distric t/ St Joseph School | 2007-02-14 | F1-3 |  | nil | clear | 138 | 522 | none | 7.74 | none | 0.68 | 0 | 0
Low Level / Social Security | 2007-02-14 | F1-4 |  | nil | clear | 145 | 615 | none | 7.81 | none | 0.33 | 0 | 0
Low / Level / I.C.C | 2007-02-19 | F1-5 |  | nil | clear | 156 | 577 | none | 7.54 | none | 0.67 | 0 | 0
North Front / Both Worlds | 2007-02-19 | F1-6 |  | nil | clear | 145 | 528 | none | 7.58 | none | 0.34 | 0 | 0
Low Level / Shell Line Wall Rd | 2007-02-27 | F1-7 |  | nil | clear | 148 | 575 | none | 7.74 | none | 0.44 | 0 | 0
Waterport / Aquagib M&E Dept | 2007-02-27 | F1-8 |  | nil | clear | 146 | 580 | none | 8.35 | none | 0.77 | 0 | 0
Low Level / Parcel Post Line Wall rd | 2007-03-07 | M1-1 |  | nil | clear | 138 | 577 | none | 8.03 | none | 0.94 | 0 | 0
High Level / Sacred Heart Church | 2007-03-07 | M1-2 |  | nil | clear | 145 | 622 | none | 8.27 | none | 0.42 | 0 | 0
Low Level / I.C.C | 2007-03-14 | M1-3 |  | nil | clear | 146 | 613 | none | 7.81 | none | 0.8 | 0 | 0
South District/Veterinary Clinic | 2007-03-14 | M1-4 |  | nil | clear | 145 | 645 | none | 7.74 | none | 0.52 | 0 | 0
Low Level / Bomb House Lane | 2007-03-20 | M1-5 |  | nil | clear | 125 | 575 | none | 7.91 | none | 0.95 | 0 | 0
North Front / Gedime Motors | 2007-03-20 | M1-6 |  | nil | clear | 110 | 506 | none | 7.92 | none | 0.96 | 0 | 0
Low Level / Social Security | 2007-03-27 | M1-7 |  | nil | clear | 147 | 608 | none | 7.14 | none | 0.65 | 0 | 0
Waterport / Electricity Dept | 2007-03-29 | M1-8 |  | nil | clear | 146 | 580 | none | 8.35 | none | 1.19 | 0 | 0
Low Level / Shell Line Wall Road | 2007-04-03 | A1-1 |  | nil | clear | 130 | 549 | none | 7.97 | none | 0.48 | 0 | 0
High Level / Flat Bastion Road | 2007-04-03 | A1-2 |  | nil | clear | 128 | 503 | none | 8.27 | none | 1.02 | 0 | 0
Low level / Gibraltar Chronicle | 2007-04-12 | A1-3 |  | nil | clear | 137 | 541 | none | 8.05 | none | 0.45 | 0 | 0
South District / The New Harbours | 2007-04-12 | A1-4 |  | nil | clear | 133 | 501 | none | 7.69 | none | 0.46 | 0 | 0
Low Level / Parcel Post | 2007-04-18 | A1-5 |  | 0.0007 | clear | 132 | 562 | none | 7.95 | none | 0.57 | 0 | 0
Reclamation / Watergardens | 2007-04-18 | A1-6 |  | 0.013 | clear | 139 | 607 | none | 8.09 | none | 0.75 | 0 | 0
Low Level / Hambros Bank | 2007-04-26 | A1-7 |  | nil | clear | 119 | 564 | none | 8.24 | none | 0.54 | 0 | 0
North Front / Toyota | 2007-04-26 | A1-8 |  | nil | clear | 108 | 458 | none | 8.42 | none | 1.33 | 0 | 0
Low Level / I.C.C | 2007-05-01 | M2-1 |  | nil | clear | 124 | 511 | none | 8.3 | none | 0.89 | 0 | 0
Waterport / Aquagib M&E Dept | 2007-05-01 | M2-2 |  | nil | clear | 109 | 462 | none | 8.6 | none | 0.38 | 0 | 0
Low level / Gibraltar Heights | 2007-05-08 | M2-3 |  | nil | clear | 119 | 491 | none | 7.8 | none | 0.46 | 0 | 0
South District / Rosia Dale | 2007-05-08 | M2-4 |  | nil | clear | 120 | 480 | none | 7.28 | none | 0.59 | 0 | 0
Low Level / Vincents Town Range | 2007-05-15 | M2-5 |  | nil | clear | 133 | 505 | none | 7.76 | none | 0.48 | 0 | 0
Reclamation / Safeway Supermarket | 2007-05-15 | M2-6 |  | nil | clear | 137 | 561 | none | 7.98 | none | 0.45 | 0 | 0
Low Level / John Mcintosh Hall | 2007-05-23 | M2-7 |  | nil | clear | 122 | 520 | none | 7.96 | none | 0.53 | 0 | 0
North Front / Gaggero Builder's | 2007-05-23 | M2-8 |  | 0.009 | clear | 127 | 536 | none | 8.02 | none | 1.01 | 0 | 0
Low level / Social Security | 2007-05-31 | M2-9 |  | nil | clear | 117 | 492 | none | 7.65 | none | 1.42 | 0 | 0
High level / Lime Kiln Steps | 2007-05-31 | M2-10 |  | nil | clear | 118 | 508 | none | 7.27 | none | 0.74 | 0 | 0
Low Level / Shell Line Wall | 2007-06-08 | J2-1 |  | nil | clear | 136 | 522 | none | 7.16 | none | 0.3 | 2 | 0
Waterport/Helm Marine | 2007-06-08 | J2-2 |  | nil | clear | 144 | 587 | none | 8.18 | none | 0.18 | 0 | 0
Low level/Parcel Post | 2007-06-13 | J2-3 |  | nil | clear | 128 | 525 | none | 7.73 | none | 0.31 | 0 | 0
South District/New Harbours | 2007-06-13 | J2-4 |  | nil | clear | 125 | 524 | none | 8.01 | none | 0.24 | 0 | 0
Low Level/I.C.C | 2007-06-20 | J2-5 |  | nil | clear | 125 | 504 | none | 7.7 | none | 0.38 | 0 | 0
Reclamation/Mcdonalds | 2007-06-20 | J2-6 |  | nil | clear | 99 | 411 | none | 7.75 | none | 0.16 | 0 | 0
Low Level /Gibraltar Chronicle | 2007-06-27 | J2-7 |  | nil | clear | 111 | 462 | none | 7.69 | none | 0.41 | 0 | 0
Low Level / social security | 2007-07-05 | J3-1 |  | nil | clear | 111 | 458 | none | 7.71 | none | 0.45 | 0 | 0
High Level / Sacred Heart | 2007-07-05 | J3-2 |  | nil | clear | 910 | 385 | none | 8.05 | none | 0.58 | 0 | 0
Low level / Gibraltar Chronicle | 2007-07-11 | J3-3 |  | nil | clear | 101 | 429 | none | 7.98 | none | 1.2 | 0 | 0
Waterport | 2007-07-11 | J3-4 |  | nil | clear | 93 | 385 | none | 8.1 | none | 0.48 | 0 | 0
Low Level / Gibraltar Heights | 2007-07-17 | J3-5 |  | nil | clear | 98 | 419 | none | 7.47 | none | 0.21 | 0 | 0
Reclamation / Varyl begg | 2007-07-17 | J3-6 |  | nil | clear | 99 | 404 | none | 7.48 | none | 0.28 | 0 | 0
L/Level /social security | 2007-07-24 | J3-7 |  | nil | clear | 103 | 424 | none | 7.9 | none | 0.92 | 0 | 0
North Front/Both Worlds | 2007-07-24 | J3-8 |  | nil | clear | 118 | 482 | none | 7.7 | none | 0.14 | 0 | 0
Low level / Social Security | 2007-07-31 | J3-9 |  | nil | clear | 108 | 443 | none | 7.78 | none | 0.97 | 0 | 0
South District / Dolphin Club | 2007-07-31 | J3-10 |  | nil | clear | 117 | 515 | none | 7.59 | none | 0.37 | 0 | 0
Low Level / Marks & Spencer | 2007-08-08 | A2-1 |  | nil | clear | 116 | 499 | none | 7.7 | none | 0.66 | 0 | 0
High Level / Carter's | 2007-08-08 | A2-2 |  | nil | clear | 136 | 577 | none | 7.87 | none | 0.31 | 0 | 0
Low level / Social Security | 2007-08-15 | A2-3 |  | nil | clear | 221 | 868 | none | 7.91 | none | 0.83 | 0 | 0
Reclamation / Varyl begg Est | 2007-08-15 | A2-4 |  | nil | clear | 115 | 492 | none | 7.81 | none | 0.31 | 0 | 0
Low Level / O'Callaghan Hotel | 2007-08-23 | A2-5 |  | nil | clear | 132 | 547 | none | 7.76 | none | 0.15 | 0 | 0
North Front / Both Worlds | 2007-08-23 | A2-6 |  | nil | clear | 102 | 428 | none | 7.64 | none | 0.15 | 0 | 0
Low Level / Social security | 2007-08-30 | A2-7 |  | nil | clear | 122 | 511 | none | 7.73 | none | 0.95 | 0 | 0
Water Port / Distiller Mess room | 2007-08-30 | A2-8 |  | nil | clear | 112 | 465 | none | 7.84 | none | 0.42 | 0 | 0
Low Level/Parcel Post | 2007-09-04 | S1-1 |  | 0.048 | clear | 116 | 488 | none | 7.71 | none | 0.93 | 0 | 0
South District/Tiny tots Nusery | 2007-09-04 | S1-2 |  | nil | clear | 123 | 506 | none | 8.05 | none | 0.39 | 0 | 0
Low level/Social Security | 2007-09-13 | S1-3 |  | nil | clear | 111 | 484 | none | 7.84 | none | 0.65 | 0 | 0
Reclamation/Safeways | 2007-09-13 | S1-4 |  | nil | clear | 117 | 479 | none | 8.02 | none | 0.58 | 0 | 0
Low Level/Gibraltar Chronicle | 2007-09-18 | S1-5 |  | nil | clear | 118 | 492 | none | 8.46 | none | 0.89 | 0 | 0
North Front/Bassadone | 2007-09-18 | S1-6 |  | nil | clear | 145 | 613 | none | 8.28 | none | 0.73 | 0 | 0
Low Level / I.C.C | 2007-09-27 | S1-7 |  | nil | clear | 140 | 548 | none | 8.14 | none | 0.24 | 0 | 0
Water Port / Helm Marine | 2007-09-27 | S1-8 |  | nil | clear | 140 | 557 | none | 8.36 | none | 0.8 | 0 | 0
Low Level / Social Security | 2007-10-02 | O1 |  | nil | clear | 122 | 523 | none | 8 | none | 0.56 | 0 | 0
High Level / Sacred Heart Church | 2007-10-04 | O2 |  | nil | clear | 117 | 473 | none | 7.92 | none | 0.36 | 0 | 0
L/level/Shell PetrolStation Line Wall | 2007-10-10 | O3 |  | nil | clear | 118 | 512 | none | 8.29 | none | 0.41 | 0 | 0
North Front/Glacis Estate | 2007-10-10 | O4 |  | nil | clear | 112 | 443 | none | 7.64 | none | 0.36 | 0 | 0
Low Level / Constitution house | 2007-10-18 | O5 |  | nil | clear | 107 | 447 | none | 7.92 | none | 0.44 | 0 | 0
Reclamation / Gov Med School | 2007-10-18 | O6 |  | nil | clear | 107 | 450 | none | 7.99 | none | 0.19 | 0 | 0
Low Level / McIntosh hall | 2007-10-23 | O7 |  | nil | clear | 166 | 621 | none | 7.97 | none | 0.2 | 0 | 0
North Front / D&H Ceramics | 2007-10-23 | O8 |  | nil | clear | 63 | 304 | none | 7.99 | none | 0.52 | 0 | 0
Low Level / Gibratlar Chronicle | 2007-10-30 | O9 |  | nil | clear | 143 | 538 | none | 7.97 | none | 0.21 | 0 | 0
Waterport / Distiller | 2007-10-30 | O10 |  | nil | clear | 146 | 581 | none | 7.99 | none | 0.64 | 0 | 0
Low Level / I.C.C | 2007-11-07 | N1 |  | nil | clear | 115 | 553 | none | 7.71 | none | 0.28 | 0 | 0
South District / New Harbours | 2007-11-07 | N2 |  | nil | clear | 154 | 633 | none | 8.09 | none | 0.26 | 0 | 0
Low level / Social Security | 2007-11-13 | N3 |  | nil | clear | 143 | 539 | none | 8.06 | none | 0.46 | 0 | 0
North Front / Glacis Estate | 2007-11-13 | N4 |  | nil | clear | 125 | 410 | none | 8.25 | none | 0.68 | 0 | 0
Low Level / Parcel post | 2007-11-21 | N5 |  | nil | clear | 129 | 535 | none | 8.2 | none | 0.46 | 0 | 0
Reclamation / Mcdonalds | 2007-11-21 | N6 |  | nil | clear | 132 | 540 | none | 8.46 | none | 0.36 | 0 | 0
Low Level / GIbraltar Chronicle | 2007-11-27 | N7 |  | nil | clear | 132 | 520 | none | 8.17 | none | 0.51 | 0 | 0
High Level / Flat bastion Rd | 2007-11-27 | N8 |  | nil | clear | 119 | 400 | none | 8.24 | none | 0.17 | 0 | 0
Low level / Social Security | 2007-12-05 | D1-1 |  | nil | clear | 115 | 434 | none | 7.71 | none | 0.28 | 0 | 0
Waterport / GibElec Power Station | 2007-12-05 | D1-2 |  | nil | clear | 152 | 629 | none | 8.09 | none | 0.26 | 0 | 0
Low level / Shell Petrol Station | 2007-12-06 | D1-3 |  | nil | clear | 119 | 460 | none | 8.32 | none | 0.26 | 0 | 0
High Level / Lime kiln Steps | 2007-12-07 | D1-4 |  | nil | clear | 125 | 463 | none | 8.01 | none | 0.22 | 0 | 0
Low Level / Gibraltar Chronicle | 2007-12-08 | D1-5 |  | nil | clear | 146 | 492 | none | 7.92 | none | 0.55 | 0 | 0
South District / Alameda House | 2007-12-09 | D1-6 |  | nil | clear | 156 | 616 | none | 8.1 | none | 0.67 | 0 | 0
Low Level / GIbraltar Chronicle | 2007-12-27 | D1-7 |  | nil | clear | 122 | 497 | none | 8.24 | none | 0.44 | 0 | 0
Reclamation / Morrisons | 2007-12-27 | D1-8 |  | nil | clear | 98 | 453 | none | 8.12 | none | 0.61 | 0 | 0
Low level / Social Security | 2007-01-02 | J4-1 |  | nil | clear | 146 | 514 | none | 8.2 | none | 1.55 | 0 | 0
North Front / Glacis Estate | 2007-01-02 | J4-2 |  | nil | clear | 148 | 579 | none | 8.37 | none | 0.37 | 0 | 0
Low level / Shell Petrol Station | 2008-01-08 | J4-3 |  | nil | clear | 144 | 502 | none | 7.99 | none | 0.41 | 0 | 0
High Level / Flat Bastion Rd | 2008-01-08 | J4-4 |  | nil | clear | 51 | 293 | none | 8.01 | none | 0.26 | 0 | 0
Low Level / Canon Lane | 2008-01-17 | J4-5 |  | nil | clear | 125 | 470 | none | 8.51 | none | 0.45 | 0 | 0
South District / Rosia dale | 2008-01-17 | J4-6 |  | nil | clear | 96 | 280 | none | 8.73 | none | 0.19 | 0 | 0
L/Level /Customs Parcel post | 2008-01-23 | J4-7 |  | nil | clear | 126 | 470 | none | 7.78 | none | 0.48 | 0 | 0
Reclamation/Eurotowers | 2008-01-23 | J4-8 |  | nil | clear | 94 | 391 | none | 7.95 | none | 0.3 | 0 | 0
Low Level / Gibratlar Chronicle | 2008-01-30 | J4-9 |  | nil | clear | 118 | 497 | none | 8.05 | none | 0.49 | 0 | 0
Waterport / Helm Marine | 2008-01-30 | J4-10 |  | nil | clear | 153 | 551 | none | 8.15 | none | 0.36 | 0 | 0
Low level / Social Security | 2008-02-05 | F2-1 |  | nil | clear | 129 | 508 | none | 8.13 | none | 0.57 | 0 | 0
High Leve / Sacred Heart Church | 2008-02-05 | F2-2 |  | nil | clear | 133 | 606 | none | 8.1 | none | 0.2 | 0 | 0
Low / level/I.C.C | 2008-02-13 | F2-3 |  | nil | clear | 123 | 487 | none | 8.51 | none | 0.22 | 0 | 0
South District / Rosia dale | 2008-02-13 | F2-4 |  | nil | clear | 122 | 500 | none | 8.85 | none | 0.61 | 0 | 0
Low Level / Parcel Post | 2008-02-19 | F2-5 |  | nil | clear | 114 | 452 | none | 8.28 | none | 0.29 | 0 | 0
North Front / Laguna Estate | 2008-02-19 | F2-6 |  | nil | clear | 98 | 369 | none | 8.27 | none | 0.36 | 0 | 0
Low Level / I.C.C | 2008-02-27 | F2-7 |  | nil | clear | 117 | 515 | none | 8.09 | none | 0.6 | 0 | 0
Reclamation / Morrisons | 2008-02-27 | F2-8 |  | nil | clear | 121 | 537 | none | 8.24 | none | 0.19 | 0 | 0
Low level / Social Security | 2008-03-05 | M3-1 |  | nil | clear | 116 | 498 | none | 8.34 | none | 0.61 | 0 | 0
Waterport / Mess room Distiller | 2008-03-05 | M3-2 |  | nil | clear | 131 | 596 | none | 8.47 | none | 0.36 | 0 | 0
Low level / Parcel Post | 2008-03-12 | M3-3 |  | nil | clear | 104 | 519 | none | 8.23 | none | 0.23 | 0 | 0
High Level / Lime Kiln Steps | 2008-03-12 | M3-4 |  | nil | clear | 55 | 313 | none | 8.28 | none | 0.08 | 0 | 0
Low level / Gibraltar chronicle | 2008-03-18 | M3-5 |  | nil | clear | 138 | 507 | none | 8.21 | none | 0.25 | 0 | 0
North Front / Glacis Estate | 2008-03-18 | M3-6 |  | nil | clear | 96 | 439 | none | 8.23 | none | 0.39 | 0 | 0
Low level / Mini-Market | 2008-03-26 | M3-7 |  | nil | clear | 138 | 491 | none | 8.45 | none | 0.55 | 0 | 0
South District / Anglo Hispano | 2008-03-26 | M3-8 |  | nil | clear | 153 | 549 | none | 8.18 | none | 0.33 | 0 | 0
Low level / Gibraltar chronicle | 2008-04-01 | A3-1 |  | nil | clear | 148 | 428 | none | 8.23 | none | 0.39 | 0 | 0
Reclamation / Mcdonald's | 2008-04-01 | A3-2 |  | nil | clear | 117 | 353 | none | 8.38 | none | 0.26 | 0 | 0
Low level / social security | 2008-04-08 | A3-3 |  | nil | clear | 118 | 367 | none | 8.15 | none | 0.3 | 0 | 0
Water Port / Helm Marine | 2008-04-08 | A3-4 |  | nil | clear | 136 | 458 | none | 8.53 | none | 0.25 | 0 | 0
Low level / Marks & Spencer | 2008-04-17 | A3-5 |  | nil | clear | 94 | 417 | none | 8.24 | none | 0.32 | 0 | 0
High Level / Police Barrack Lane | 2008-04-17 | A3-6 |  | nil | clear | 40 | 223 | none | 8.51 | none | 0.19 | 0 | 0
Low level / social security | 2008-04-24 | A3-7 |  | nil | clear | 111 | 468 | none | 8.23 | none | 0.24 | 0 | 0
North Front / both worlds | 2008-04-24 | A3-8 |  | nil | clear | 123 | 346 | none | 8.37 | none | 0.41 | 0 | 0
Low level / Parcel post | 2008-04-29 | A3-9 |  | nil | clear | 134 | 478 | none | 8.2 | none | 0.25 | 0 | 0
South District / New Harbours | 2008-04-29 | A3-10 |  | nil | clear | 138 | 579 | none | 8.21 | none | 0.36 | 0 | 0
Low level / Gibraltar chronicle | 2008-05-07 | M4-1 |  | nil | clear | 146 | 480 | none | 8.16 | none | 0.31 | 0 | 0
High Level / Arengo's palace | 2008-05-07 | M4-2 |  | nil | clear | 132 | 367 | none | 8.59 | none | 0.28 | 0 | 0
Low level / I.C.C | 2008-05-14 | M4-3 |  | nil | clear | 152 | 484 | none | 8.18 | none | 0.26 | 0 | 0
North Front / Both worlds | 2008-05-14 | M4-4 |  | nil | clear | 64 | 293 | none | 8.02 | none | 0.39 | 0 | 0
Low level / Social Security | 2008-05-21 | M4-5 |  | nil | clear | 99 | 505 | none | 7.83 | none | 0.36 | 0 | 0
South District / Scud Hill | 2008-05-21 | M4-6 |  | nil | clear | 72 | 378 | none | 8.46 | none | 0.66 | 0 | 0
Lowl evel / Gibraltar chronicle | 2008-05-29 | M4-7 |  | nil | clear | 119 | 480 | none | 8.21 | none | 0.46 | 0 | 0
Reclamation / Morrisons | 2008-05-29 | M4-8 |  | nil | clear | 89 | 371 | none | 8.13 | none | 0.38 | 0 | 0
L/level/Irish Town | 2008-06-05 | J5-1 |  | nil | clear | 165 | 475 | none | 8.09 | none | 0.33 | 0 | 0
Waterport/Distiller | 2008-06-05 | J5-2 |  | nil | clear | 170 | 617 | none | 8.37 | none | 0.41 | 0 | 0
L/level/social security | 2008-06-11 | J5-3 |  | nil | clear | 137 | 483 | none | 7.99 | none | 0.35 | 0 | 0
High Level/Lime Kiln Steps | 2008-06-11 | J5-4 |  | nil | clear | 8.23 | 273 | none | 8.23 | none | 0.25 | 0 | 0
Low level / Parcel post | 2008-06-18 | J5-5 |  | nil | clear | 120 | 414 | none | 7.81 | none | 0.63 | 0 | 0
North Front / Glacis Estate | 2008-06-18 | J5-6 |  | nil | clear | 88 | 634 | none | 8.04 | none | 0.26 | 0 | 0
Low level / Gibraltar chronicle | 2008-06-24 | J5-7 |  | 0.008 | clear | 127 | 455 | none | 7.91 | none | 0.44 | 0 | 0
South District / Anglo Hispano | 2008-06-24 | J5-8 |  | nil | clear | 170 | 610 | none | 8.11 | none | 0.21 | 0 | 0
Low level / social security | 2008-07-02 | J6-1 |  | nil | clear | 140 | 546 | none | 7.71 | none | 0.63 | 0 | 0
Reclamation / McDonalds | 2008-07-02 | J6-2 |  | nil | clear | 119 | 496 | none | 7.79 | none | 0.88 | 0 | 0
Low level / Parcel post | 2008-07-08 | J6-3 |  | 0.004 | clear | 135 | 563 | none | 7.65 | none | 0.28 | 0 | 0
Waterport / Power Station | 2008-07-08 | J6-4 |  | nil | clear | 131 | 566 | none | 8.27 | none | 0.19 | 0 | 0
Low level /John Mack Hall | 2008-07-15 | J6-5 |  | nil | clear | 116 | 487 | none | 8.2 | none | 0.23 | 0 | 0
High Level / Lime Kiln Steps | 2008-07-15 | J6-6 |  | nil | clear | 91 | 421 | none | 8.35 | none | 0.88 | 0 | 0
Low level / Gibraltar chronicle | 2008-07-22 | J6-7 |  | nil | clear | 126 | 466 | none | 7.74 | none | 0.2 | 0 | 0
South District / South Pavilion Road | 2008-07-22 | J6-8 |  | nil | clear | 122 | 507 | none | 7.98 | none | 0.26 | 0 | 0
Low level / Mill Pharmacy | 2008-07-29 | J6-9 |  | nil | clear | 122 | 374 | none | 7.82 | none | 0.31 | 0 | 0
North Front / Victoria Stadium | 2008-07-29 | J6-10 |  | nil | clear | 92 | 378 | none | 7.92 | none | 0.36 | 0 | 0
Low level / Shell Petrol Station | 2008-08-05 | A4-1 |  | nil | clear | 116 | 483 | none | 7.83 | none | 0.15 | 0 | 0
Reclamation / Morrisons | 2008-08-05 | A4-2 |  | nil | clear | 169 | 625 | none | 7.73 | none | 0.19 | 0 | 0
Low level / Social Security | 2008-08-12 | A4-3 |  | nil | clear | 93 | 465 | none | 7.98 | none | 0.45 | 0 | 0
South District / South Pavilion Road | 2008-08-12 | A4-4 |  | nil | clear | 159 | 454 | none | 8.05 | none | 0.18 | 0 | 0
Low level / Amar's Bakery | 2008-08-20 | A4-5 |  | nil | clear | 83 | 386 | none | 8.08 | none | 0.29 | 0 | 0
Waterport / Electricity Gen St | 2008-08-20 | A4-6 |  | nil | clear | 79 | 373 | none | 8.19 | none | 0.47 | 0 | 0
Low level / GibChronicle | 2008-08-28 | A4-7 |  | nil | clear | 113 | 478 | none | 8.01 | none | 0.19 | 0 | 0
Reclamation / Morrisons | 2008-08-28 | A4-8 |  | nil | clear | 172 | 614 | none | 7.87 | none | 0.19 | 0 | 0
Low level / Social Security | 2008-09-04 | S2-1 |  | nil | clear | 135 | 551 | none | 8.17 | none | 0.35 | 0 | 0
High Level / Lime Kiln steps | 2008-09-04 | S2-2 |  | nil | clear | 197 | 733 | none | 8.25 | none | 0.29 | 0 | 0
Lower level / Gibraltar Chronicle | 2008-09-11 | S2-3 |  | nil | clear | 150 | 646 | none | 8.03 | none | 0.35 | 0 | 0
North Front / Glacis Estate | 2008-09-11 | S2-4 |  | nil | clear | 170 | 722 | none | 8.08 | none | 0.2 | 0 | 0
Lower Level / Hospital Steps | 2008-09-17 | S2-5 |  | nil | clear | 172 | 685 | none | 8.29 | none | 0.41 | 0 | 0
Waterport / Distiller Mess room | 2008-09-18 | S2-6 |  | nil | clear | 153 | 689 | none | 8.42 | none | 0.2 | 0 | 0
Lower Level / Social Security | 2008-09-24 | S2-7 |  | nil | clear | 170 | 689 | none | 8.06 | none | 0.41 | 0 | 0
South District / Police compound | 2008-09-24 | S2-8 |  | nil | yellow | 180 | 712 | none | 8.37 | none | 5.84 | 0 | 0
Lower Level / Parcel Post | 2008-10-01 | O2-1 |  | nil | clear | 166 | 636 | none | 7.94 | none | 0.29 | 0 | 0
Reclamation / Mc Donald's | 2008-10-01 | O2-2 |  | nil | clear | 168 | 635 | none | 8.2 | none | 0.19 | 0 | 0
Lower level / Social security | 2008-10-08 | O2-3 |  | nil | clear | 166 | 683 | none | 8.32 | none | 0.46 | 0 | 0
North front / Bassadone | 2008-10-08 | O2-4 |  | nil | clear | 172 | 677 | none | 8.59 | none | 0.34 | 0 | 0
Lower Level / Sterling Travel | 2008-10-16 | O2-5 |  | nil | clear | 188 | 680 | none | 8.15 | none | 0.38 | 0 | 0
Waterport / Distiller Canteen | 2008-10-16 | O2-6 |  | nil | clear | 166 | 635 | none | 8.27 | none | 0.31 | 0 | 0
Lower level / Social security | 2008-10-22 | O2-7 |  | nil | clear | 190 | 644 | none | 8.34 | none | 0.39 | 0 | 0
South District / New habours | 2008-10-22 | O2-8 |  | nil | clear | 203 | 709 | none | 8.44 | none | 0.41 | 0 | 0
Lower level / John McIntosh Hall | 2008-10-30 | O2-9 |  | nil | clear | 94 | 371 | none | 8.67 | none | 1.76 | 0 | 0
High Level / Police Barracks | 2008-10-30 | O2-10 |  | nil | clear | 194 | 341 | none | 8.59 | none | 0.44 | 0 | 0
Lower level / Gibraltar Chronicle | 2008-11-04 | N2-1 |  | nil | clear | 160 | 553 | none | 8.28 | none | 0.41 | 0 | 0
Reclamation / Westside School | 2008-11-04 | N2-2 |  | nil | clear | 178 | 518 | none | 8.49 | none | 0.31 | 0 | 0
Lower leve / Parcel post | 2008-11-11 | N2-3 |  | nil | clear | 162 | 581 | none | 8.37 | none | 0.33 | 0 | 0
WaterPort / Distiller Canteen | 2008-11-11 | N2-4 |  | nil | clear | 167 | 549 | none | 8.39 | none | 0.41 | 0 | 0
Lower Level / Amar's Bakery | 2008-11-18 | N2-5 |  | nil | clear | 170 | 592 | none | 7.96 | none | 0.36 | 0 | 0
High Leve l/ Flat Bastion Road | 2008-11-18 | N2-6 |  | nil | clear | 180 | 596 | none | 8.16 | none | 0.26 | 0 | 0
Lower level / Mcintosh Hall | 2008-11-27 | N2-7 |  | nil | clear | 159 | 587 | none | 8.14 | none | 0.38 | 0 | 0
Westside / Oceanvillage | 2008-11-27 | N2-8 |  | nil | clear | 180 | 640 | none | 8.81 | none | 0.46 | 0 | 0
Lower level / Parcel Post | 2008-12-04 | D2-1 |  | nil | clear | 147 | 561 | none | 8.46 | none | 0.45 | 0 | 0
North Front / Both Worlds | 2008-12-04 | D2-2 |  | nil | clear | 153 | 590 | none | 8.41 | none | 0.31 | 0 | 0
Lower level / Cornwall's Parade | 2008-12-09 | D2-3 |  | nil | clear | 158 | 577 | none | 8.54 | none | 0.66 | 0 | 0
Recalmantion / Morrisons | 2008-12-09 | D2-4 |  | nil | clear | 176 | 624 | none | 8.54 | none | 0.53 | 0 | 0
Lower level / Parcel Post | 2008-12-15 | D2-5 |  | nil | clear | 150 | 563 | none | 8.07 | none | 0.53 | 0 | 0
Waterport / Helm marine | 2008-12-15 | D2-6 |  | nil | clear | 136 | 472 | none | 8.37 | none | 0.2 | 0 | 0
Lower level / Gibraltar Chronicle | 2008-12-29 | D2-7 |  | nil | clear | 173 | 640 | none | 8.4 | none | 0.56 | 0 | 0
South district / Anglo Hispano | 2008-12-29 | D2-8 |  | nil | clear | 168 | 606 | none | 7.62 | none | 0.39 | 0 | 0
Lower level / Social Security | 2009-01-08 | J7-1 |  | nil | clear | 158 | 556 | none | 8.29 | none | 0.48 | 0 | 0
North front / Glacis Estate | 2009-01-08 | J7-2 |  | nil | clear | 165 | 605 | none | 8.48 | none | 0.38 | 0 | 0
Lower Level / Parcel Post | 2009-01-14 | J7-3 |  | nil | clear | 159 | 601 | none | 8.2 | none | 1.07 | 0 | 0
High Level / Lime Kiln Steps | 2009-01-14 | J7-4 |  | nil | clear | 164 | 617 | none | 8.24 | none | 0.85 | 0 | 0
Lower Level / Gibraltar Chronicle | 2009-01-20 | J7-5 |  | nil | clear | 164 | 628 | none | 8.01 | none | 0.79 | 0 | 0
Reclamation / Mcdonald's | 2009-01-20 | J7-6 |  | nil | clear | 160 | 637 | none | 8.3 | none | 0.39 | 0 | 0
Lower Level / Amar Bakery | 2009-01-28 | J7-7 |  | nil | clear | 155 | 579 | none | 8.15 | none | 0.59 | 0 | 0
Waterport / Gib Elec Power station | 2009-01-28 | J7-8 |  | nil | clear | 163 | 642 | none | 8.32 | none | 0.41 | 0 | 0
South District/New Harbours | 2009-02-03 | F3-1 |  | nil | clear | 160 | 598 | none | 8.18 | none | 0.17 | 0 | 0
Low Level -Social Security | 2009-02-03 | F3-2 |  | nil | clear | 182 | 871 | none | 8.26 | none | 0.37 | 0 | 0
North front /Bassadone | 2009-02-11 | F3-3 |  | nil | clear | 173 | 646 | none | 8.43 | none | 0.39 | 0 | 0
Low Level - Gibraltar Chronicle | 2009-02-11 | F3-4 |  | nil | clear | 169 | 622 | none | 8.38 | none | 0.44 | 0 | 0
Reclamation/Harbour views | 2009-02-17 | F3-5 |  | nil | clear | 183 | 609 | none | 8.15 | none | 0.68 | 0 | 0
Low Level - Town Range | 2009-02-17 | F3-6 |  | nil | clear | 166 | 623 | none | 8.03 | none | 0.51 | 0 | 0
South District/Cumberland | 2009-02-26 | F3-7 |  | nil | clear | 178 | 630 | none | 8.51 | none | 0.44 | 0 | 0
Low Level / I.C.C | 2009-02-26 | F3-8 |  | nil | clear | 179 | 617 | none | 8.16 | none | 0.39 | 0 | 0
North Front / Glacis Estate | 2009-03-04 | M3-1 |  | nil | clear | 173 | 653 | none | 8.41 | none | 0.39 | 0 | 0
Low Level / Department of education | 2009-03-04 | M3-2 |  | nil | clear | 170 | 633 | none | 8.44 | none | 0.46 | 0 | 0
High Leve l/ S.Heart church | 2009-03-11 | M3-4 |  | nil | Yellow | 165 | 615 | none | 8.31 | none | 1.58 | 0 | 0
Low Level / Parcel Post | 2009-03-11 | M3-5 |  | nil | Yellow | 181 | 643 | none | 8.35 | none | 1.02 | 0 | 0
Waterport / M & E Kitchen | 2009-03-18 | M3-7 |  | nil | clear | 108 | 471 | none | 9.83 | none | 0.22 | 0 | 0
Low Level / Social Security | 2009-03-18 | M3-8 |  | nil | clear | 145 | 566 | none | 8.45 | none | 0.59 | 0 | 0
South District / New Harbours | 2009-03-29 | M3-10 |  | 0.057 | clear | 176 | 647 | none | 7.76 | none | 0.26 | 0 | 0
Low Level / Gibraltar Chornicle | 2009-03-29 | M3-11 |  | 0.056 | clear | 144 | 562 | none | 7.86 | none | 0.88 | 0 | 0
Reclamation / Varyl Begg | 2009-03-31 | M3-13 |  | 0.018 | clear | 191 | 678 | none | 7.85 | none | 0.39 | 0 | 0
Low Level / Parcel Post | 2009-03-31 | M3-14 |  | 0.013 | clear | 151 | 580 | none | 7.72 | none | 0.56 | 0 | 0
North Front / Both Worlds | 2009-04-07 | A5-1 |  | nil | clear | 188 | 695 | none | 8.14 | none | 0.59 | 0 | 0
Low Level / Gibraltar Chronicle | 2009-04-07 | A5-2 |  | nil | clear | 169 | 666 | none | 7.93 | none | 0.42 | 0 | 0
North Front / Both Worlds | 2009-04-14 | A5-4 |  | nil | clear | 190 | 669 | none | 8.37 | none | 0.29 | 0 | 0
Low Level / Parcel Post | 2009-04-14 | A5-5 |  | nil | clear | 169 | 628 | none | 8.29 | none | 0.19 | 0 | 0
High Level / Lime Kiln Steps | 2009-04-23 | A5-7 |  | 0.024 | clear | 189 | 688 | none | 8.19 | none | 0.33 | 0 | 0
Low Level / Social Security | 2009-04-23 | A5-8 |  | 0.02 | clear | 183 | 652 | none | 8.14 | none | 0.29 | 0 | 0
Waterport / Helm Marine Ltd | 2009-04-28 | A5-10 |  | 0.09 | clear | 177 | 644 | none | 8.07 | none | 1.37 | 0 | 0
Low Level / Gibraltar Chronicle | 2009-04-28 | A5-11 |  | nil | clear | 168 | 634 | none | 8.32 | none | 0.95 | 0 | 0
High Level / Arengo's Palace | 2009-05-05 | M6-1 |  | nil | clear | 185 | 627 | none | 8 | none | 0.9 | 0 | 0
Low Level / Social Security | 2009-05-05 | M6-2 |  | nil | clear | 182 | 624 | none | 7.98 | none | 0.81 | 0 | 0
North Front / Glacis Estate | 2009-05-13 | M6-4 |  | nil | clear | 184 | 677 | none | 8.33 | none | 0.29 | 0 | 0
Low Level / Gibraltar chronicle | 2009-05-13 | M6-5 |  | nil | clear | 175 | 669 | none | 8.28 | none | 0.59 | 0 | 0
South District / E.T.Board | 2009-05-21 | M6-6 |  | nil | clear | 186 | 687 | none | 8.32 | none | 0.86 | 0 | 0
Low Level / St Mary's First School | 2009-05-21 | M6-7 |  | nil | clear | 168 | 667 | none | 8.23 | none | 0.17 | 0 | 0
Reclamation / Morrisons | 2009-05-27 | M6-8 |  | nil | clear | 179 | 679 | none | 8.25 | none | 0.39 | 0 | 0
Low Level / Gibraltar chronicle | 2009-05-27 | M6-9 |  | nil | clear | 170 | 677 | none | 8.24 | none | 0.88 | 0 | 0
North front / Lancaster Road | 2009-06-02 | J8-1 |  | nil | clear | 192 | 710 | none | 8.17 | none | 0.3 | 0 | 0
Low Level / Social Security | 2009-06-02 | J8-2 |  | nil | clear | 183 | 689 | none | 8.13 | none | 0.49 | 0 | 0
High Level / Flast Bastion Rd | 2009-06-09 | J8-5 |  | nil | clear | 173 | 666 | none | 8.3 | none | 0.41 | 0 | 0
Low Level / Parcel Post | 2009-06-09 | J8-5 |  | nil | clear | 177 | 669 | none | 8.28 | none | 0.78 | 0 | 0
Reclamation / Grant Thornton | 2009-06-18 | J8-7 |  | nil | clear | 188 | 637 | none | 8.5 | none | 0.16 | 0 | 0
Low Level / Gibraltar chronicle | 2009-06-18 | J8-8 |  | nil | clear | 157 | 594 | none | 8.2 | none | 0.41 | 0 | 0
South district / South Barrack | 2009-06-23 | J8-10 |  | 0.003 | clear | 180 | 691 | none | 8.17 | none | 0.1 | 0 | 0
Low Level / Social Security | 2009-06-23 | J8-11 |  | nil | clear | 178 | 683 | none | 8.66 | none | 0.9 | 0 | 0
Water Port / Gib Elec | 2009-07-01 | J9-1 |  | nil | clear | 154 | 599 | none | 7.92 | none | 0.13 | 0 | 0
Low Level / Town Range | 2009-07-01 | J9-2 |  | nil | clear | 188 | 671 | none | 8.11 | none | 1.03 | 0 | 0
Soth District / South Pav Rd | 2009-07-08 | J9-4 |  | 0.001 | clear | 173 | 658 | none | 8.14 | none | 0.1 | 0 | 0
Low Level / Gib Chronicle | 2009-07-08 | J9-5 |  | nil | clear | 172 | 703 | none | 8.01 | none | 0.15 | 0 | 0
Reclamation/Montagu cresent | 2009-07-14 | J9-7 |  | nil | clear | 202 | 739 | none | 8.16 | none | 0.33 | 0 | 0
Low Level / Social Security | 2009-07-14 | J9-8 |  | nil | clear | 191 | 687 | none | 7.92 | none | 0.1 | 0 | 0
North Front / Devils Tower Road | 2009-07-23 | J9-10 |  | nil | clear | 191 | 719 | none | 8.1 | none | 0.26 | 0 | 0
Low Level / Dept of Education | 2009-07-23 | J9-11 |  | nil | clear | 190 | 659 | none | 8.03 | none | 0.29 | 0 | 0
High Level / Prince Edwards Road | 2009-07-28 | J9-13 |  | 0.008 | clear | 189 | 706 | none | 8.1 | none | 0.15 | 0 | 0
Low Level / Gib Chronicle | 2009-07-28 | J9-14 |  | nil | clear | 191 | 718 | none | 8.2 | none | 0.9 | 0 | 0
Waterport | 2009-08-04 | A5-1 |  | nil | clear | 206 | 754 | none | 8.42 | none | 0.28 | 0 | 0
Low Level / Cornwall Centre | 2009-08-04 | A5-2 |  | nil | clear | 190 | 723 | none | 8.16 | none | 0.3 | 0 | 0
South District / South Pavilion Road | 2009-08-12 | A5-4 |  | nil | clear | 193 | 746 | none | 8.21 | none | 0.12 | 0 | 0
Low Level / Gib Chronicle | 2009-08-12 | A5-5 |  | nil | clear | 200 | 765 | none | 8.14 | none | 0.14 | 0 | 0
Reclamation / Morrisons | 2009-08-20 | A5-7 |  | nil | clear | 210 | 759 | none | 8.36 | none | 0.14 | 0 | 0
Low Level / Shell Petrol Station | 2009-08-20 | A5-8 |  | nil | clear | 205 | 744 | none | 8.39 | none | 0.18 | 0 | 0
South District / Sandpits House | 2009-08-25 | A5-10 |  | nil | clear | 221 | 766 | none | 8.25 | none | 0.18 | 0 | 0
Low Level / Leanse House | 2009-08-25 | A5-11 |  | nil | clear | 214 | 776 | none | 8.25 | none | 0.22 | 0 | 0
North Front / Glacis Estate | 2009-09-01 | S3-1 |  | nil | clear | 213 | 747 | none | 8.22 | none | 0.26 | 0 | 0
Low Level / Parcel Post | 2009-09-01 | S3-2 |  | nil | clear | 217 | 771 | none | 7.69 | none | 0.31 | 0 | 0
Reclamation / Morrisons Superstore | 2009-09-08 | S3-4 |  | nil | clear | 199 | 678 | none | 7.99 | none | 0.22 | 0 | 0
Low Level / Gibraltar chronicle | 2009-09-08 | S3-5 |  | nil | clear | 193 | 675 | none | 8.08 | none | 0.39 | 0 | 0
South District / Cumberland Rd | 2009-09-15 | S3-7 |  | nil | clear | 203 | 788 | none | 8.1 | none | 0.36 | 0 | 0
Low Level / Social security | 2009-09-15 | S3-8 |  | nil | clear | 193 | 766 | none | 7.88 | none | 0.44 | 0 | 0
Waterport / Distiller Plant Canteen | 2009-09-22 | S3-10 |  | nil | clear | 194 | 734 | none | 8.09 | none | 0.13 | 0 | 0
Low Level / Gibraltar chronicle | 2009-09-22 | S3-11 |  | nil | clear | 206 | 743 | none | 8.04 | none | 0.42 | 0 | 0
High Level / Arengo's Steps | 2009-09-30 | S3-13 |  | nil | clear | 201 | 728 | none | 7.82 | none | 0.34 | 0 | 0
Low Level / Social security | 2009-09-30 | S3-14 |  | nil | clear | 207 | 727 | none | 7.6 | none | 0.39 | 0 | 0
North front / Devil's tower Rd | 2009-10-06 | O3-1 |  | nil | clear | 196 | 744 | none | 8.12 | none | 0.15 | 0 | 0
Low Level / Gibraltar Chronicle | 2009-10-06 | O3-2 |  | nil | clear | 195 | 738 | none | 7.97 | none | 0.37 | 0 | 0
Waterport / Port Dept. | 2009-10-13 | O3-4 |  | nil | clear | 199 | 761 | none | 8.06 | none | 0.16 | 0 | 0
Low Level / Amar's Bakery | 2009-10-13 | O3-5 |  | nil | clear | 211 | 750 | none | 8.11 | none | 0.37 | 0 | 0
Reclamation / Harbour views | 2009-10-20 | O3-7 |  | nil | clear | 202 | 729 | none | 7.87 | none | 0.09 | 0 | 0
Low Level / Parcel Post | 2009-10-20 | O3-8 |  | nil | clear | 197 | 740 | none | 7.84 | none | 0.28 | 0 | 0
South District / Francis Garage | 2009-10-27 | O3-10 |  | 0.009 | clear | 202 | 721 | none | 8.27 | none | 0.31 | 0 | 0
Low Level / Gibraltar Chronicle | 2009-10-27 | O3-11 |  | nil | clear | 202 | 734 | none | 8.03 | none | 0.25 | 0 | 0
South district / schonberg | 2009-11-03 | N3-1 |  | nil | clear | 211 | 723 | none | 8.01 | none | 0.36 | 0 | 0
Low Level / Parcel Post | 2009-11-03 | N3-2 |  | nil | clear | 206 | 723 | none | 7.87 | none | 0.84 | 0 | 0
High Level / Lime kiln steps | 2009-11-10 | N3-4 |  | nil | clear | 185 | 684 | none | 8.14 | none | 0.42 | 0 | 0
Low Level / social security | 2009-11-10 | N3-5 |  | nil | clear | 196 | 701 | none | 8.03 | none | 0.92 | 0 | 0
Reclamation / West view park | 2009-11-18 | N3-7 |  | nil | clear | 190 | 695 | none | 8.33 | none | 0.41 | 0 | 0
Low Level / Gibraltar Chronicle | 2009-11-18 | N3-8 |  | nil | clear | 182 | 676 | none | 8.15 | none | 0.81 | 0 | 0
Waterport / M & E mess room | 2009-11-24 | N3-10 |  | 0.005 | clear | 207 | 745 | none | 8.22 | none | 0.61 | 0 | 0
Low Level / Social security | 2009-11-24 | N3-11 |  | 0.008 | clear | 205 | 737 | none | 8.26 | none | 0.21 | 0 | 0
North Front / Both worlds | 2009-12-02 | D3-1 |  | 0.008 | clear | 202 | 726 | none | 8.21 | none | 0.44 | 0 | 0
Low Level / Amar Bakery | 2009-12-02 | D3-2 |  | 0.01 | clear | 207 | 700 | none | 8.14 | none | 0.91 | 0 | 0
High level / Flat bastion Rd | 2009-12-08 | D3-4 |  | nil | clear | 201 | 707 | none | 8.18 | none | 0.17 | 0 | 0
Low Level / Social Security | 2009-12-08 | D3-5 |  | nil | clear | 208 | 732 | none | 7.73 | none | 0.67 | 0 | 0
North Front / Glacis Estate | 2009-12-15 | D3-7 |  | nil | clear | 176 | 666 | none | 8.25 | none | 0.33 | 0 | 0
Low Level / St. Mary's School | 2009-12-14 | D3-8 |  | nil | clear | 169 | 619 | none | 7.73 | none | 0.95 | 0 | 0
Reclamation / Hire-u-shop | 2009-12-21 | D3-10 |  | nil | clear | 203 | 709 | none | 8.14 | none | 0.39 | 0 | 0
Low Level / Parcel Post | 2009-12-21 | D3-11 |  | nil | clear | 177 | 614 | none | 7.9 | none | 0.79 | 0 | 0
Waterport / M & E Depot | 2009-12-29 | D3-13 |  | 0.002 | clear | 115 | 442 | none | 8.16 | none | 0.4 | 0 | 0
Low Level / Social Security | 2009-12-29 | D3-14 |  | nil | clear | 174 | 629 | none | 7.9 | none | 0.76 | 0 | 0
South District / Scud Hill | 2010-01-06 | J10-1 |  | nil | clear | 197 | 694 | none | 8.35 | none | 0.36 | 0 | 0
Low Level / Gibraltar chronicle | 2010-01-06 | J10-2 |  | nil | clear | 191 | 611 | none | 7.81 | none | 0.81 | 0 | 0
High Level / Sacred Heart Church | 2010-01-13 | J10-4 |  | nil | clear | 200 | 700 | none | 7.92 | none | 0.43 | 0 | 0
Low Level / Social Security | 2010-01-13 | J10-5 |  | nil | clear | 184 | 618 | none | 7.74 | none | 0.96 | 0 | 0
North Front / Devil's Tower rd | 2010-01-19 | J10-7 |  | nil | clear | 200 | 703 | none | 8.22 | none | 0.41 | 0 | 0
Low Level / Amar's Bakery | 2010-01-19 | J10-8 |  | nil | clear | 191 | 671 | none | 8.29 | none | 0.71 | 0 | 0
South District / New Harbour | 2010-01-26 | J10-10 |  | 0.003 | clear | 198 | 682 | none | 7.91 | none | 0.16 | 0 | 0
Low Level / Gibraltar chronicle | 2010-01-26 | J10-11 |  | 0.002 | clear | 190 | 654 | none | 7.81 | none | 0.49 | 0 | 0
Reclamation / Morrisons Superstore | 2010-02-02 | F4-1 |  | nil | clear | 183 | 679 | none | 8.12 | none | 0.33 | 0 | 0
Low Level / Amar's Bakery | 2010-02-02 | F4-2 |  | 0.014 | clear | 189 | 695 | none | 8.11 | none | 0.63 | 0 | 0
High Level / Flat Bastion Rd | 2010-02-09 | F4-4 |  | nil | clear | 182 | 700 | none | 7.86 | none | 0.74 | 0 | 0
Low Level / Social Security | 2010-02-09 | F4-5 |  | nil | clear | 179 | 669 | none | 7.84 | none | 0.95 | 0 | 0
Waterport / Helm marine | 2010-02-16 | F4-7 |  | nil | clear | 180 | 662 | none | 8.4 | none | 0.31 | 0 | 0
Low Level / Gibraltar chronicle | 2010-02-16 | F4-8 |  | nil | clear | 178 | 663 | none | 8.24 | none | 0.62 | 0 | 0
North Front / Both worlds | 2010-02-23 | F4-10 |  | nil | clear | 181 | 663 | none | 8.42 | none | 0.44 | 0 | 0
Low Level / I.C.C | 2010-02-23 | F4-11 |  | nil | clear | 176 | 629 | none | 8.17 | none | 0.75 | 0 | 0
South District / Mi-Fix Cumb Rd | 2010-03-02 | M7-1 |  | 0.004 | clear | 193 | 695 | none | 8.43 | none | 0.39 | 0 | 0
Low Level / Social security | 2010-03-02 | M7-2 |  | 0.012 | clear | 184 | 634 | none | 8.29 | none | 0.81 | 0 | 0
Reclamation / Watergardens2 | 2010-03-09 | M7-4 |  | nil | clear | 176 | 624 | none | 7.98 | none | 0.39 | 0 | 0
Low Level / Gibraltar chronicle | 2010-03-09 | M7-5 |  | nil | clear | 186 | 641 | none | 8.21 | none | 0.89 | 0 | 0
High Level / Sacred heart school | 2010-03-16 | M7-7 |  | nil | clear | 179 | 668 | none | 8.82 | none | 0.47 | 0 | 0
Low Level / Amar's Bakery | 2010-03-16 | M7-8 |  | nil | clear | 170 | 640 | none | 8.68 | none | 0.42 | 0 | 0
North Front / Glacis estate | 2010-03-23 | M7-10 |  | nil | clear | 202 | 726 | none | 8.34 | none | 0.36 | 0 | 0
Low Level / Gibraltar chronicle | 2010-03-23 | M7-11 |  | nil | clear | 187 | 672 | none | 8.28 | none | 0.44 | 0 | 0
High Level / flat bastion Rd | 2010-04-06 | A7-1 |  | nil | clear | 194 | 719 | none | 8.19 | none | 0.33 | 0 | 0
Low Level / Town Range | 2010-04-06 | A7-2 |  | nil | clear | 187 | 679 | none | 8.09 | none | 0.55 | 0 | 0
North front / Glacis Estate | 2010-04-13 | A7-4 |  | nil | clear | 198 | 718 | none | 8.44 | none | 0.36 | 0 | 0
Low Level / Social Security | 2010-04-13 | A7-5 |  | nil | clear | 195 | 711 | none | 8.3 | none | 0.79 | 0 | 0
South District / New Harbours | 2010-04-20 | A7-7 |  | nil | clear | 203 | 729 | none | 8.35 | none | 0.36 | 0 | 0
Low Level / Gibraltar Chronicle | 2010-04-20 | A7-8 |  | nil | clear | 196 | 724 | none | 8.36 | none | 0.38 | 0 | 0
Reclamation / Edinbourgh house | 2010-04-27 | A7-10 |  | nil | clear | 195 | 749 | none | 8.28 | none | 0.36 | 0 | 0
Low Level / McIntosh Hall | 2010-04-27 | A7-11 |  | nil | clear | 193 | 726 | none | 8.27 | none | 0.61 | 0 | 0
Waterport / Aquagib M&E depot | 2010-05-04 | M8-1 |  | nil | clear | 217 | 788 | none | 8.17 | none | 0.41 | 0 | 0
Low Level / Social Security | 2010-05-04 | M8-2 |  | 0.006 | clear | 205 | 766 | none | 8.17 | none | 0.66 | 0 | 0
North front / Glacis Estate | 2010-05-11 | M8-4 |  | nil | clear | 187 | 750 | none | 8.27 | none | 0.41 | 0 | 0
Low Level / Gibraltar chronicle | 2010-05-11 | M8-5 |  | nil | clear | 205 | 751 | none | 8.37 | none | 0.33 | 0 | 0
High Level / Arengos steps | 2010-05-18 | M8-7 |  | nil | clear | 195 | 729 | none | 8.29 | none | 0.31 | 0 | 0
Low Level / Social security | 2010-05-18 | M8-8 |  | nil | clear | 193 | 725 | none | 8.17 | none | 0.48 | 0 | 0
North front / Laguna estate | 2010-05-25 | M8-10 |  | nil | clear | 204 | 678 | none | 8.42 | none | 0.66 | 0 | 0
Low Level / I.C.C | 2010-05-25 | M8-11 |  | nil | clear | 220 | 798 | none | 8.11 | none | 0.57 | 0 | 0
South district / Grand parade | 2010-06-01 | J11-1 |  | nil | clear | 215 | 756 | none | 8.07 | none | 0.68 | 0 | 0
Low Level / Social security | 2010-06-01 | J11-2 |  | nil | clear | 206 | 778 | none | 8.15 | none | 0.77 | 0 | 0
Reclamation / Harbour views | 2010-06-08 | J11-4 |  | nil | clear | 211 | 743 | none | 8.08 | none | 0.29 | 0 | 0
Level Low / Town range | 2010-06-08 | J11-5 |  | nil | clear | 207 | 710 | none | 8.09 | none | 0.41 | 0 | 0
High level / Sacred heart school | 2010-06-18 | J11-7 |  | 0.009 | clear | 188 | 682 | none | 7.93 | none | 0.66 | 0 | 0
Low Level / John Mcintosh Hall | 2010-06-18 | J11-8 |  | 0.013 | clear | 203 | 738 | none | 8.03 | none | 0.71 | 0 | 0
North front / Bassadone | 2010-06-22 | J11-10 |  | nil | clear | 203 | 717 | none | 8.23 | none | 0.31 | 0 | 0
Low Level / Gibraltar Chronicle | 2010-06-22 | J11-11 |  | 0.005 | clear | 201 | 735 | none | 8.16 | none | 0.49 | 0 | 0
Water port / Shipping main / Distiller | 2010-06-29 | J11-13 |  | 0 | clear | 199 | 733 | none | 8.11 | none | 0.46 | 0 | 0
Low Level / Social security | 2010-06-29 | J11-14 |  | 0.01 | clear | 195 | 698 | none | 8.31 | none | 0.81 | 0 | 0
North front / Catalan bay | 2010-07-06 | J12-1 |  | nil | clear | 8.36 | 723 | none | 8.36 | none | 0.35 | 0 | 0
Low Level / Gibraltar chronicle | 2010-07-06 | J12-2 |  | nil | clear | 8.29 | 713 | none | 8.29 | none | 0.57 | 0 | 0
South District / St.Josephs School | 2010-07-14 | J12-4 |  | nil | clear | 216 | 733 | none | 8.14 | none | 0.22 | 0 | 0
Low Level / Macintosh Hall | 2010-07-14 | J12-5 |  | nil | clear | 190 | 674 | none | 7.76 | none | 0.6 | 0 | 0
South District / Car Care Centre | 2010-07-20 | J12-7 |  | nil | clear | 213 | 754 | none | 8.16 | none | 0.53 | 0 | 0
Low Level / Amar Bakery | 2010-07-20 | J12-8 |  | nil | clear | 199 | 706 | none | 8.29 | none | 0.39 | 0 | 0
Water Port / M & E Dept | 2010-07-27 | J12-10 |  | nil | clear | 196 | 702 | none | 8.22 | none | 0.36 | 0 | 0
Low Level / Macintosh Hall | 2010-07-27 | J12-11 |  | nil | clear | 191 | 695 | none | 8.06 | none | 0.25 | 0 | 0
Reclamation / Montague Pavillion | 2010-08-03 | A8-1 |  | nil | clear | 192 | 663 | none | 8.05 | none | 0.42 | 0 | 0
Low Level / I.CC | 2010-08-03 | A8-2 |  | nil | clear | 193 | 673 | none | 7.7 | none | 0.36 | 0 | 0
Reclamation / Morrisons Superstore | 2010-08-10 | A8-4 |  | nil | clear | 205 | 780 | none | 8.1 | none | 0.33 | 0 | 0
Low Level / Angry Friar | 2010-08-10 | A8-5 |  | nil | clear | 210 | 686 | none | 8.1 | none | 0.22 | 0 | 0
North Front / Glacis Store | 2010-08-18 | A8-7 |  | nil | clear | 195 | 693 | none | 7.98 | none | 0.36 | 0 | 0
Low Level / Social Security | 2010-08-18 | A8-8 |  | nil | clear | 182 | 689 | none | 8.05 | none | 0.49 | 0 | 0
Waterport / Gib ElecPower Station | 2010-08-24 | A8-10 |  | nil | clear | 188 | 657 | none | 7.93 | none | 0.43 | 0 | 0
Low Level / John Macintosh Hall | 2010-08-24 | A8-11 |  | nil | clear | 181 | 631 | none | 7.6 | none | 0.25 | 0 | 0
South District / St Joseph M School | 2010-09-09 | S4-1 |  | 0.03 | clear | 201 | 699 | none | 8.12 | none | 0.19 | 0 | 0
Low Level / St Mary's School | 2010-09-09 | S4-2 |  | 0.02 | clear | 174 | 613 | none | 7.9 | none | 0.43 | 0 | 0
Waterport / Gib Elec Power Station | 2010-09-15 | S4-4 |  | nil | clear | 130 | 481 | none | 8.01 | none | 0.46 | 0 | 0
Low Level / John McIntosh Hall | 2010-09-15 | S4-5 |  | nil | clear | 153 | 561 | none | 7.62 | none | 0.31 | 0 | 0
North Front / Devils Tower Road | 2010-09-22 | S4-7 |  | 0.01 | clear | 206 | 738 | none | 8.12 | none | 0.36 | 0 | 0
Low Level / Social Security Dept | 2010-09-22 | S4-8 |  | nil | clear | 197 | 691 | none | 8.14 | none | 0.32 | 0 | 0
Reclamation / Albert Risso | 2010-09-28 | S4-10 |  | nil | clear | 191 | 681 | none | 8.12 | none | 0.28 | 0 | 0
Low Level / Gibraltar chronicle | 2010-09-28 | S4-11 |  | nil | clear | 168 | 662 | none | 7.71 | none | 0.46 | 0 | 0
High Level / Flat Bastion Rd | 2010-10-06 | O4-1 |  | nil | clear | 165 | 600 | none | 8.23 | none | 0.36 | 0 | 0
Low Level / Amar's Bakery | 2010-10-06 | O4-2 |  | nil | clear | 181 | 611 | none | 7.96 | none | 0.64 | 0 | 0
North Front / Devil's Tower Rd | 2010-10-12 | O4-4 |  | nil | clear | 198 | 687 | none | 8.19 | none | 0.16 | 0 | 0
Low Level / John McIntosh Hall | 2010-10-12 | O4-5 |  | nil | clear | 175 | 635 | none | 7.95 | none | 0.32 | 0 | 0
Reclamation / New Harbours | 2010-10-19 | O4-7 |  | nil | clear | 136 | 473 | none | 7.97 | none | 0.31 | 0 | 0
Low Level / Social Security | 2010-10-19 | O4-8 |  | nil | clear | 161 | 628 | none | 7.91 | none | 0.44 | 0 | 0
Waterport/ Aquagib Distiller Kitchen | 2010-10-26 | O4-10 |  | nil | clear | 207 | 720 | none | 8.13 | none | 0.33 | 0 | 0
Low Level / GibraltarChronicle | 2010-10-26 | O4-11 |  | nil | clear | 144 | 512 | none | 7.36 | none | 0.61 | 0 | 0
High Level / Arengo's steps | 2010-11-02 | N4-1 |  | nil | clear | 112 | 385 | none | 8.23 | none | 0.28 | 0 | 0
Low Level / McIntosh hall | 2010-11-02 | N4-2 |  | nil | clear | 102 | 388 | none | 8.02 | none | 0.36 | 0 | 0
Reclamation / Morrisons Superstore | 2010-11-09 | N4-4 |  | 0.01 | clear | 161 | 588 | none | 8.31 | none | 0.16 | 0 | 0
Low Level / Gibraltar Chronicle | 2010-11-09 | N4-5 |  | 0.012 | clear | 171 | 623 | none | 7.83 | none | 0.39 | 0 | 0
North front / Glacis estate | 2010-11-16 | N4-7 |  | 0.001 | clear | 180 | 651 | none | 8.31 | none | 0.27 | 0 | 0
Low Level / Town range | 2010-11-16 | N4-8 |  | 0.008 | clear | 165 | 621 | none | 8.04 | none | 0.88 | 0 | 0
South district / Alameda Estate | 2010-11-23 | N4-10 |  | 0.002 | clear | 197 | 699 | none | 7.58 | none | 0.34 | 0 | 0
Low Level / I.C.C | 2010-11-23 | N4-11 |  | 0.001 | clear | 192 | 677 | none | 7.43 | none | 0.57 | 0 | 0
Reclamation / Waterport | 2010-11-30 | N4-13 |  | nil | clear | 192 | 665 | none | 8.28 | none | 0.25 | 0 | 0
Low Level / Social security | 2010-11-30 | N4-14 |  | nil | clear | 186 | 647 | none | 7.9 | none | 0.59 | 0 | 0
High Level / Sacred heart School | 2010-12-08 | D4-1 |  | nil | clear | 201 | 707 | none | 8.23 | none | 0.25 | 0 | 0
Low Level / Education Dept. | 2010-12-08 | D4-2 |  | nil | clear | 180 | 616 | none | 8.19 | none | 0.39 | 0 | 0
Reclamation / Peninsula Heights | 2010-12-14 | D4-4 |  | nil | clear | 203 | 738 | none | 8.5 | none | 0.32 | 0 | 0
Low Level / Gibraltar Chronicle | 2010-12-14 | D4-5 |  | nil | clear | 178 | 660 | none | 8.41 | none | 0.47 | 0 | 0
South District / New Harbours | 2010-12-21 | D4-7 |  | nil | clear | 175 | 581 | none | 8.46 | none | 0.36 | 0 | 0
Low Level / Social Security | 2010-12-21 | D4-8 |  | nil | clear | 189 | 718 | none | 8.32 | none | 0.72 | 0 | 0
North front / Devil's Tower Rd | 2010-12-29 | D4-10 |  | nil | clear | 176 | 633 | none | 8.14 | none | 0.32 | 0 | 0
Low Level / I.C.C | 2010-12-29 | D4-11 |  | nil | clear | 171 | 682 | none | 8.07 | none | 0.51 | 0 | 0
South District - Rosia Dale | 2011-01-04 | J11-1 |  | nil | clear | 197 | 698 | none | 8.48 | none | 0.38 | 0 | 0
Low Level / Gibraltar chronicle | 2011-01-04 | J11-2 |  | nil | clear | 173 | 666 | none | 8.32 | none | 0.59 | 0 | 0
Reclamation / Waterport terraces | 2011-01-11 | J11-4 |  | nil | clear | 196 | 752 | none | 8.36 | none | 0.41 | 0 | 0
Low Level / Social Security | 2011-01-11 | J11-5 |  | nil | clear | 176 | 688 | none | 8.11 | none | 0.79 | 0 | 0
Waterport / North mole | 2011-01-18 | J11-4 |  | nil | clear | 204 | 684 | none | 8.59 | none | 0.14 | 0 | 0
Low Level / ICC | 2011-01-18 | J11-5 |  | nil | clear | 177 | 589 | none | 8.58 | none | 0.21 | 0 | 0
High level / flat Bastion Rd | 2011-01-25 | J11-10 |  | nil | clear | 142 | 467 | none | 8.72 | none | 0.34 | 0 | 0
Low Level / Gibraltar chronicle | 2011-01-25 | J11-11 |  | 0.02 | clear | 237 | 780 | none | 8.38 | none | 0.56 | 0 | 0
North Front / Glacis Estate | 2011-02-01 | F5-1 |  | nil | clear | 210 | 720 | none | 8.36 | none | 0.36 | 0 | 0
Low Level / Amar's Bakery | 2011-02-01 | F5-2 |  | nil | clear | 206 | 749 | none | 8.28 | none | 0.67 | 0 | 0
South District / Scud Hill | 2011-02-09 | F5-4 |  | nil | clear | 211 | 724 | none | 8.37 | none | 0.26 | 0 | 0
Low Level / Gibraltar chronicle | 2011-02-09 | F5-5 |  | nil | clear | 242 | 884 | none | 8.16 | none | 0.3 | 0 | 0
Waterport / Port authority | 2011-02-18 | F5-7 |  | nil | clear | 204 | 733 | none | 8.21 | none | 0.33 | 0 | 0
Low Level / McIntosh hall | 2011-02-18 | F5-8 |  | nil | clear | 298 | 1054 | none | 8.19 | none | 0.46 | 0 | 0
High level / Arengo's palace | 2011-02-22 | F5-10 |  | nil | clear | 200 | 715 | none | 8.56 | none | 0.21 | 0 | 0
Low Level / Social security | 2011-02-22 | F5-11 |  | 0.01 | clear | 195 | 712 | none | 8.19 | none | 0.3 | 0 | 0
Reclamation / Mcdonald's | 2011-03-02 | M9-1 |  | nil | clear | 206 | 700 | none | 8.57 | none | 0.19 | 0 | 0
Low Level / Gibraltar chronicle | 2011-03-02 | M9-2 |  | nil | clear | 177 | 653 | none | 8.34 | none | 0.46 | 0 | 0
North Front / Filomena house | 2011-03-11 | M9-4 |  | nil | clear | 205 | 730 | none | 8.32 | none | 0.26 | 0 | 0
Low Level / Central police station | 2011-03-11 | M9-5 |  | nil | clear | 166 | 614 | none | 8.36 | none | 0.38 | 0 | 0
South District / New harbours | 2011-03-16 | M9-7 |  | nil | clear | 189 | 715 | none | 8.55 | none | 0.26 | 0 | 0
Low Level / John McIntosh hall | 2011-03-16 | M9-8 |  | nil | clear | 163 | 605 | none | 8.33 | none | 0.3 | 0 | 0
Reclamation / Morrisons | 2011-03-22 | M9-10 |  | nil | clear | 184 | 681 | none | 8.22 | none | 0.14 | 0 | 0
Low Level / Education Dept. | 2011-03-23 | M9-11 |  | nil | clear | 147 | 543 | none | 8.47 | none | 0.7 | 0 | 0
High level / Lime kiln steps | 2011-03-30 | M9-13 |  | nil | clear | 208 | 741 | none | 8.49 | none | 0.25 | 0 | 0
Low Level / Gibraltar chronicle | 2011-03-30 | M9-14 |  | 0.01 | clear | 140 | 516 | none | 8.44 | none | 0.44 | 0 | 0
North front / Both worlds | 2011-04-05 | A9-1 |  | nil | clear | 209 | 761 | none | 8.32 | none | 0.34 | 0 | 0
Low Level / Social security | 2011-04-05 | A9-2 |  | nil | clear | 179 | 631 | none | 8.24 | none | 0.95 | 0 | 0
Waterport / Helm Marine | 2011-04-12 | A9-4 |  | nil | clear | 211 | 759 | none | 8.47 | none | 0.25 | 0 | 0
Low Level / Amar's bakery | 2011-04-12 | A9-5 |  | nil | clear | 174 | 615 | none | 8.23 | none | 0.36 | 0 | 0
South District / Alameda Kiosk | 2011-04-19 | A9-7 |  | nil | clear | 212 | 753 | none | 8.37 | none | 0.24 | 0 | 0
Low Level / John Mcintosh Hall | 2011-04-19 | A9-8 |  | nil | clear | 177 | 625 | none | 8.18 | none | 0.46 | 0 | 0
Reclamation / Mid-harbour estate | 2011-04-26 | A9-10 |  | nil | clear | 201 | 716 | none | 8.46 | none | 0.31 | 0 | 0
Low Level / Gibraltar chronicle | 2011-04-26 | A9-11 |  | nil | clear | 160 | 587 | none | 8.1 | none | 0.47 | 0 | 0
Waterport / Distiller messroom | 2011-05-03 | M10-1 |  | nil | clear | 166 | 616 | none | 8.15 | none | 0.56 | 0 | 0
Low Level / Amar's Bakery | 2011-05-03 | M10-2 |  | nil | clear | 215 | 748 | none | 8.3 | none | 0.29 | 0 | 0
North front / Glacis estate | 2011-05-10 | M10-4 |  | nil | clear | 217 | 763 | none | 8.34 | none | 0.15 | 0 | 0
Low Level / I.C.C | 2011-05-10 | M10-5 |  | nil | clear | 180 | 657 | none | 8.22 | none | 0.3 | 0 | 0
Reclamation / Morrisons | 2011-05-18 | M10-7 |  | nil | clear | 204 | 746 | none | 8.24 | none | 0.21 | 0 | 0
Low Level / Gibraltar chronicle | 2011-05-18 | M10-8 |  | nil | clear | 188 | 697 | none | 8.02 | none | 0.25 | 0 | 0
South District / New harbours | 2011-05-24 | M10-10 |  | nil | clear | 219 | 787 | none | 8.23 | none | 0.22 | 0 | 0
Low Level / Police station | 2011-05-24 | M10-11 |  | nil | clear | 204 | 730 | none | 8.2 | none | 0.28 | 0 | 0
High level / Dannino's Ramp | 2011-06-01 | J13-1 |  | nil | clear | 216 | 788 | none | 8.09 | none | 0.14 | 0 | 0
Low Level / Gibraltar Collage | 2011-06-01 | J13-2 |  | nil | clear | 212 | 777 | none | 8.08 | none | 0.26 | 0 | 0
High level / Flat Bastion Rd | 2011-06-08 | J13-4 |  | 0.024 | clear | 211 | 780 | none | 8.29 | none | 0.17 | 0 | 0
Low Level / Central Police Station | 2011-06-08 | J13-5 |  | 0.032 | clear | 206 | 572 | none | 8.32 | none | 0.45 | 0 | 0
Reclamation / West View park | 2011-06-15 | J13-7 |  | nil | clear | 214 | 774 | none | 8.3 | none | 0.26 | 0 | 0
Low Level / Social Security | 2011-06-15 | J13-8 |  | nil | clear | 202 | 773 | none | 8.02 | none | 0.38 | 0 | 0
Waterport / Aquagib M&E Depot | 2011-06-22 | J13-10 |  | nil | clear | 215 | 785 | none | 7.48 | none | 0.28 | 0 | 0
Low Level / Environmental Agency | 2011-06-22 | J13-11 |  | nil | clear | 204 | 753 | none | 7.53 | none | 0.47 | 0 | 0
South District / Scud Hill | 2011-06-29 | J13-13 |  | nil | clear | 224 | 743 | none | 8.2 | none | 0.18 | 0 | 0
Low Level / Gibraltar chronicle | 2011-06-29 | J13-14 |  | nil | clear | 197 | 689 | none | 8.19 | none | 0.48 | 0 | 0
North Front / Both Worlds | 2011-07-06 | J14-1 |  | nil | clear | 214 | 811 | none | 7.95 | none | 0.38 | 0 | 0
Low Level / Social Security | 2011-07-06 | J14-2 |  | nil | clear | 178 | 676 | none | 8.13 | none | 0.79 | 0 | 0
South District / Mi Fix Garage | 2011-07-12 | J14-4 |  | nil | clear | 207 | 753 | none | 7.97 | none | 0.29 | 0 | 0
Low Level / Amar's bakery | 2011-07-12 | J14-5 |  | nil | clear | 190 | 679 | none | 8.22 | none | 0.37 | 0 | 0
High Level / Leanse place | 2011-07-19 | J14-7 |  | nil | clear | 187 | 702 | none | 7.91 | none | 0.85 | 0 | 0
Low Level / Central Police station | 2011-07-19 | J14-8 |  | nil | clear | 195 | 681 | none | 7.92 | none | 0.28 | 0 | 0
North Front / North view terrace | 2011-07-26 | J14-10 |  | 0.005 | clear | 200 | 711 | none | 8.15 | none | 0.38 | 0 | 0
Low Level / Mini-Market | 2011-07-26 | J14-11 |  | 0.011 | clear | 197 | 698 | none | 8.05 | none | 0.58 | 0 | 0
Reclamation / Europort | 2011-08-03 | A10-1 |  | nil | clear | 206 | 755 | none | 8.14 | none | 0.1 | 0 | 0
Low Level / St Mary's first school | 2011-08-03 | A10-2 |  | nil | clear | 187 | 683 | none | 8.11 | none | 0.31 | 0 | 0
Waterport / Port Authority | 2011-08-08 | A10-4 |  | nil | clear | 203 | 729 | none | 8.28 | none | 0.14 | 0 | 0
Low Level / John Mackintosh Hall | 2011-08-08 | A10-5 |  | nil | clear | 190 | 696 | none | 8.16 | none | 0.28 | 0 | 0
High Level / Flat Bastion Road | 2011-08-16 | A10-7 |  | nil | clear | 208 | 747 | none | 8.2 | none | 0.16 | 0 | 0
Low Level / Shell Petrol Station | 2011-08-16 | A10-8 |  | nil | clear | 191 | 689 | none | 7.96 | none | 0.3 | 0 | 0
Reclamation / Morrisons | 2011-08-24 | A10-10 |  | nil | clear | 186 | 675 | none | 7.95 | none | 0.14 | 0 | 0
Low Level / Engineer's lane | 2011-08-24 | A10-11 |  | nil | S.Rusty | 195 | 689 | none | 7.95 | none | 0.48 | 0 | 0
South District / Scud hill | 2011-08-30 | A10-13 |  | nil | clear | 200 | 723 | none | 7.94 | none | 0.25 | 0 | 0
Low Level / I.C.C Ground floor | 2011-08-30 | A10-14 |  | nil | clear | 141 | 521 | none | 7.73 | none | 0.34 | 0 | 0
North Front / Glacis estate | 2011-09-06 | S5-1 |  | nil | clear | 232 | 750 | none | 8.57 | none | 0.41 | 0 | 0
Low Level / Social Security | 2011-09-06 | S5-2 |  | nil | clear | 174 | 536 | none | 8.12 | none | 0.59 | 0 | 0
Reclamation/Harbour views | 2011-09-14 | S5-4 |  | nil | clear | 210 | 744 | none | 8.53 | none | 0.3 | 0 | 0
Low Level / Gibraltar chronicle | 2011-09-14 | S5-5 |  | 0.01 | clear | 185 | 639 | none | 8.09 | none | 0.46 | 0 | 0
South District / New harbours | 2011-09-22 | S5-7 |  | nil | clear | 219 | 769 | none | 8.42 | none | 0.31 | 0 | 0
Low Level / Amar's Bakery | 2011-09-22 | S5-8 |  | nil | clear | 189 | 669 | none | 8.12 | none | 0.46 | 0 | 0
Waterport / Helm Marine | 2011-09-29 | S5-10 |  | 0.01 | clear | 217 | 772 | none | 8.29 | none | 0.34 | 0 | 0
Low Level / I.C.C | 2011-09-29 | S5-11 |  | nil | clear | 194 | 686 | none | 8.11 | none | 0.24 | 0 | 0
High Level / Arengo's Palace | 2011-10-05 | O5-1 |  | nil | clear | 224 | 783 | none | 8.32 | none | 0.33 | 0 | 0
Low Level / Social Security | 2011-10-05 | O5-2 |  | nil | clear | 183 | 617 | none | 8.12 | none | 0.62 | 0 | 0
Reclamation / Mid-habour | 2011-10-11 | O5-4 |  | nil | clear | 182 | 654 | none | 8.27 | none | 0.14 | 0 | 0
Low Level / Gibraltar Chronicle | 2011-10-11 | O5-5 |  | nil | clear | 183 | 633 | none | 8.2 | none | 0.31 | 0 | 0
Water port / Aquagib M&E Dept | 2011-10-19 | O5-7 |  | nil | clear | 221 | 781 | none | 8.36 | none | 0.17 | 0 | 0
Low Level / Amar's Bakery | 2011-10-19 | O5-8 |  | nil | clear | 181 | 694 | none | 8.29 | none | 0.34 | 0 | 0
Reclamation / Waterport terraces | 2011-10-25 | O5-10 |  | nil | clear | 222 | 774 | none | 8.31 | none | 0.37 | 0 | 0
Low Level / Social Security Dept. | 2011-10-25 | O5-11 |  | nil | clear | 221 | 734 | none | 8.19 | none | 0.19 | 0 | 0
North front / Glacis estate | 2011-11-01 | N5-1 |  | nil | clear | 223 | 766 | none | 8.19 | none | 0.19 | 0 | 0
Low Level / I.C.C | 2011-11-01 | N5-2 |  | nil | clear | 210 | 740 | none | 8.22 | none | 0.39 | 0 | 0
South District / Scud hill | 2011-11-09 | N5-4 |  | nil | clear | 208 | 695 | none | 8.15 | none | 0.19 | 0 | 0
Low Level / Department Education | 2011-11-09 | N5-5 |  | nil | clear | 211 | 734 | none | 8.06 | none | 0.39 | 0 | 0
North Front / Laguna estate | 2011-11-15 | N5-7 |  | nil | clear | 221 | 711 | none | 8.2 | none | 0.37 | 0 | 0
Low Level / Amarr Bakery | 2011-11-15 | N5-8 |  | nil | clear | 216 | 731 | none | 8.05 | none | 0.41 | 0 | 0
High Level / Sacred heart | 2011-11-23 | N5-10 |  | 0.028 | clear | 216 | 732 | none | 8.27 | none | 0.36 | 0 | 0
Low Level / Social security | 2011-11-23 | N5-11 |  | nil | clear | 217 | 712 | none | 8.07 | none | 0.39 | 0 | 0
Reclamation / Morrisons | 2011-11-29 | N5-13 |  | nil | clear | 215 | 775 | none | 8.07 | none | 0.31 | 0 | 0
Low Level / Gibraltar chronicle | 2011-11-29 | N5-14 |  | nil | clear | 205 | 740 | none | 8.25 | none | 0.66 | 0 | 0
North Front / Devil's Tower Rd | 2011-12-06 | D5-1 |  | nil | clear | 204 | 784 | none | 8.43 | none | 0.35 | 0 | 0
Low Level / Social Security | 2011-12-06 | D5-2 |  | nil | clear | 212 | 763 | none | 8.25 | none | 0.58 | 0 | 0
North Front / Both Worlds | 2011-12-14 | D5-4 |  | nil | clear | 203 | 718 | none | 8.21 | none | 0.33 | 0 | 0
Low Level / Amarr's Bakery | 2011-12-14 | D5-5 |  | nil | clear | 202 | 758 | none | 8.06 | none | 0.56 | 0 | 0
Reclamation / WaterGardens | 2011-12-21 | D5-7 |  | nil | clear | 212 | 820 | none | 8.14 | none | 0.17 | 0 | 0
Low Level / John McIntosh Hall | 2011-12-21 | D5-8 |  | 0.01 | clear | 215 | 767 | none | 7.9 | none | 0.24 | 0 | 0
High Level / Flat Bastion road | 2011-12-28 | D5-10 |  | 0.02 | clear | 219 | 809 | none | 8.24 | none | 0.31 | 0 | 0
Low Level / I.C.C | 2011-12-28 | D5-11 |  | 0.01 | clear | 228 | 797 | none | 8.15 | none | 0.49 | 0 | 0
North front / Glacis estate | 2012-01-05 | J16-1 |  | nil | clear | 221 | 814 | none | 7.93 | none | 0.33 | 0 | 0
Low Level / Public Market | 2012-01-05 | J16-2 |  | nil | clear | 215 | 800 | none | 7.83 | none | 0.61 | 0 | 0
South District / St Joesph | 2012-01-11 | J16-4 |  | nil | clear | 221 | 765 | none | 8.21 | none | 0.18 | 0 | 0
Low Level / College | 2012-01-11 | J16-5 |  | 0.01 | clear | 218 | 741 | none | 7.95 | none | 0.31 | 0 | 0
North front / Glacis estate | 2012-01-16 | J16-7 |  | nil | clear | 207 | 763 | none | 8.08 | none | 0.14 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-01-16 | J16-8 |  | nil | clear | 216 | 759 | none | 7.87 | none | 0.33 | 0 | 0
WaterPort / M&E Dept | 2012-01-24 | J16-10 |  | nil | clear | 220 | 788 | none | 7.2 | none | 0.24 | 0 | 0
Low Level / St Marys Middle School | 2012-01-24 | J16-11 |  | nil | clear | 214 | 778 | none | 7.21 | none | 0.14 | 0 | 0
Reclamation / Gov Med School | 2012-01-30 | J16-13 |  | nil | clear | 204 | 729 | none | 7.79 | none | 0.15 | 0 | 0
Low Level / Mcintosh Hall | 2012-01-30 | J16-14 |  | nil | clear | 218 | 772 | none | 7.89 | none | 0.18 | 0 | 0
North FrontDevils Tower Rd Auto stop | 2012-02-10 | F6-1 |  | nil | clear | 200 | 697 | none | 8.05 | none | 0.15 | 0 | 0
Low Level /Central Police Stn Irish Twn | 2012-02-10 | F6-2 |  | nil | clear | 211 | 742 | none | 8.04 | none | 0.45 | 0 | 0
South District / Alameda kiosk | 2012-02-14 | F6-4 |  | nil | clear | 208 | 765 | none | 8.04 | none | 0.33 | 0 | 0
Low Level / Social security | 2012-02-14 | F6-5 |  | nil | clear | 204 | 748 | none | 8 | none | 0.55 | 0 | 0
North Front / Boths worlds | 2012-02-22 | F6-7 |  | nil | clear | 220 | 773 | none | 8.24 | none | 0.31 | 0 | 0
Low Level / Amar's Bakery | 2012-02-22 | F6-8 |  | 0.03 | clear | 210 | 746 | none | 8.2 | none | 0.6 | 0 | 0
High Level -Arengo's Palace | 2012-02-28 | F6-10 |  | nil | clear | 214 | 726 | none | 8.18 | none | 0.28 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-02-28 | F6-11 |  | nil | clear | 209 | 756 | none | 8.01 | none | 0.26 | 0 | 0
Reclamation / Mid-Harbour estate | 2012-03-07 | M11-1 |  | nil | clear | 210 | 738 | none | 8.17 | none | 0.21 | 0 | 0
Low Level / John McIntosh Hall | 2012-03-07 | M11-2 |  | nil | clear | 204 | 715 | none | 8.1 | none | 0.39 | 0 | 0
South District / St Joseph school | 2012-03-14 | M11-4 |  | nil | clear | 200 | 750 | none | 8.28 | none | 0.33 | 0 | 0
Low Level / Central Police Station | 2012-03-14 | M11-5 |  | nil | clear | 197 | 758 | none | 8.2 | none | 0.58 | 0 | 0
High Level / Willis' Road | 2012-03-22 | M11-7 |  | nil | clear | 203 | 743 | none | 8.28 | none | 0.13 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-03-19 | M11-8 |  | 0.009 | clear | 199 | 693 | none | 8.21 | none | 0.07 | 0 | 0
North Front / Glacis Estate | 2012-03-27 | M11-10 |  | nil | clear | 203 | 718 | none | 8.27 | none | 0.29 | 0 | 0
Low Level / Amar's bakery | 2012-03-27 | M11-11 |  | 0.009 | clear | 197 | 735 | none | 8.19 | none | 0.67 | 0 | 0
Reclamation / Harbour Views | 2012-04-03 | A11-1 |  | nil | clear | 206 | 748 | none | 7.87 | none | 0.26 | 0 | 0
Low Level / John McIntosh Hall | 2012-04-03 | A11-2 |  | nil | clear | 200 | 749 | none | 7.97 | none | 0.71 | 0 | 0
Waterport / Gib Elec. | 2012-04-10 | A11-4 |  | 0.007 | clear | 216 | 802 | none | 8.54 | none | 0.31 | 0 | 0
Low Level / Town Range | 2012-04-10 | A11-5 |  | 0.007 | clear | 206 | 786 | none | 8.21 | none | 0.5 | 0 | 0
NorthFront / Both Worlds | 2012-04-18 | A11-7 |  | nil | clear | 199 | 766 | none | 8.22 | none | 0.34 | 0 | 0
Low Level / Social Security | 2012-04-18 | A11-8 |  | nil | clear | 203 | 754 | none | 8.1 | none | 0.42 | 0 | 0
South District / St Josephs Scl | 2012-04-24 | A11-10 |  | nil | clear | 207 | 709 | none | 8.13 | none | 0.16 | 0 | 0
Low Level / I.C.C | 2012-04-24 | A11-11 |  | nil | clear | 201 | 692 | none | 7.94 | none | 0.36 | 0 | 0
M.C Estate / 17 Keighteley House | 2012-05-02 | M12-1 |  | 0.01 | clear | 207 | 700 | none | 7.63 | none | 0.25 | 0 | 0
Low Level / John McIntosh Hall | 2012-05-02 | M12-2 |  | 0.01 | clear | 207 | 700 | none | 7.67 | none | 0.28 | 0 | 0
Reclamation / Harbour Views | 2012-05-07 | M12-4 |  | nil | clear | 201 | 687 | none | 8.1 | none | 0.12 | 0 | 0
Low Level / City Hall | 2012-05-07 | M12-5 |  | nil | clear | 206 | 697 | none | 7.92 | none | 0.84 | 0 | 0
NorthFront / Cemetery toilet | 2012-05-14 | M12-7 |  | 0.04 | clear | 201 | 684 | none | 7.93 | none | 0.16 | 0 | 0
Low Level / Gib Chronicle | 2012-05-14 | M12-8 |  | 0.04 | clear | 210 | 704 | none | 7.67 | none | 0.29 | 0 | 0
Waterport / Gib Elec | 2012-05-24 | M12-10 |  | nil | clear | 207 | 776 | none | 7.97 | none | 0.32 | 0 | 0
Low Level / St. Mary's Middle School | 2012-05-24 | M12-11 |  | nil | clear | 205 | 767 | none | 7.93 | none | 0.36 | 0 | 0
South District / Alameda Estate | 2012-05-30 | M12-13 |  | nil | clear | 194 | 793 | none | 8.15 | none | 0.12 | 0 | 0
Low Level / ICC | 2012-05-30 | M12-14 |  | nil | clear | 165 | 778 | none | 8.05 | none | 0.29 | 0 | 0
Waterport / Gib Oil | 2012-06-06 | J17-1 |  | nil | clear | 208 | 769 | none | 7.74 | none | 0.23 | 0 | 0
Low Level / John McIntosh Hall | 2012-06-06 | J17-2 |  | nil | clear | 207 | 776 | none | 7.68 | none | 0.3 | 0 | 0
South District- Fire Brigade G.Parade | 2012-06-13 | J17-4 |  | 0.062 | clear | 218 | 800 | none | 8.17 | none | 0.23 | 0 | 0
Low Level / Central Police Station | 2012-06-13 | J17-5 |  | 0.001 | clear | 211 | 778 | none | 8.07 | none | 0.59 | 0 | 0
High Level / Willis's Road | 2012-06-20 | J17-7 |  | nil | clear | 219 | 798 | none | 7.99 | none | 0.23 | 0 | 0
Low Level-College | 2012-06-20 | J17-8 |  | nil | clear | 222 | 808 | none | 7.51 | none | 0.59 | 0 | 0
Reclamation / Morrisons Superstore | 2012-06-26 | J17-10 |  | nil | clear | 219 | 790 | none | 8.01 | none | 0.27 | 0 | 0
Low Level / Casemates- Burger King | 2012-06-26 | J17-11 |  | nil | clear | 214 | 779 | none | 8.01 | none | 0.49 | 0 | 0
North Front / Glacis Estate | 2012-07-03 | J18-1 |  | nil | clear | 205 | 749 | none | 7.96 | none | 0.45 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-07-03 | J18-2 |  | nil | clear | 215 | 772 | none | 7.92 | none | 0.5 | 0 | 0
Waterport / Redwood | 2012-07-10 | J18-4 |  | 0.032 | clear | 215 | 796 | none | 8.24 | none | 0.52 | 0 | 0
Low Level / Mackintosh Hall | 2012-07-10 | J18-5 |  | 0.023 | clear | 213 | 779 | none | 8.02 | none | 0.4 | 0 | 0
South District / Fire Brigade | 2012-07-17 | J18-7 |  | nil | clear | 219 | 787 | none | 8.24 | none | 0.42 | 0 | 0
Low Level / Central Police Station | 2012-07-17 | J18-8 |  | nil | clear | 213 | 767 | none | 8.02 | none | 0.74 | 0 | 0
High Level / Sacred Heart School | 2012-07-24 | J18-10 |  | 0.002 | clear | 219 | 765 | none | 7.3 | none | 0.23 | 0 | 0
Low Level / College | 2012-07-24 | J18-11 |  | 0.027 | clear | 213 | 759 | none | 7.23 | none | 0.2 | 0 | 0
Reclamation / Morrisons | 2012-07-31 | J18-13 |  | nil | clear | 219 | 788 | none | 7.26 | none | 0.23 | 0 | 0
Low Level / Casemates / Burger King | 2012-07-31 | J18-14 |  | nil | clear | 219 | 760 | none | 7.32 | none | 0.2 | 0 | 0
North Front / Glacis Estate | 2012-08-07 | A12-1 |  | 0.004 | clear | 222 | 765 | none | 7.35 | none | 0.22 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-08-07 | A12-2 |  | 0.011 | clear | 216 | 742 | none | 7.4 | none | 0.44 | 0 | 0
Waterport / Redwood | 2012-08-14 | A12-4 |  | 0.026 | clear | 221 | 771 | none | 7.48 | none | 0.21 | 0 | 0
Low Level / Mackintosh Hall | 2012-08-14 | A12-5 |  | 0.026 | clear | 223 | 762 | none | 7.46 | none | 0.4 | 0 | 0
South District / Fire Brigade | 2012-08-21 | A12-7 |  | nil | clear | 211 | 728 | none | 8.02 | none | 0.32 | 0 | 0
Low Level / Central Police Station | 2012-08-21 | A12-8 |  | 0.003 | clear | 218 | 774 | none | 8.02 | none | 0.61 | 0 | 0
High Level / Sacred Heart School | 2012-08-28 | A12-10 |  | 0.003 | clear | 217 | 767 | none | 8.14 | none | 0.63 | 0 | 0
Low Level / College | 2012-08-28 | A12-11 |  | 0.001 | clear | 215 | 767 | none | 7.67 | none | 0.66 | 0 | 0
North Front / Glacis Estate | 2012-09-04 | S6-1 |  | nil | clear | 217 | 766 | none | 7.76 | none | 0.89 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-09-04 | S6-2 |  | nil | clear | 217 | 770 | none | 7.6 | none | 0.3 | 0 | 0
Waterport / Redwood | 2012-09-11 | S6-4 |  | nil | clear | 241 | 860 | none | 8.13 | none | 0.21 | 0 | 0
Low Level / Mackintosh Hall | 2012-09-11 | S6-5 |  | nil | clear | 218 | 786 | none | 7.87 | none | 0.23 | 0 | 0
South District / Fire Brigade | 2012-09-18 | S6-7 |  | nil | clear | 220 | 792 | none | 8.2 | none | 0.2 | 0 | 0
Low Level / Central Police Station | 2012-09-18 | S6-8 |  | nil | clear | 225 | 805 | none | 7.96 | none | 0.63 | 0 | 0
High Level / Sacred Heart School | 2012-09-24 | S6-10 |  | nil | clear | 222 | 794 | none | 8.13 | none | 0.71 | 0 | 0
Low Level / College | 2012-09-24 | S6-11 |  | nil | clear | 222 | 806 | none | 7.7 | none | 0.35 | 0 | 0
North Front / Devils Tower Road | 2012-10-02 | O6-1 |  | nil | clear | 210 | 753 | none | 7.97 | none | 0.29 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-10-02 | O6-2 |  | nil | clear | 217 | 783 | none | 7.79 | none | 0.37 | 0 | 0
Waterport / Redwood | 2012-10-09 | O6-4 |  | 0.014 | clear | 217 | 786 | none | 8.02 | none | 0.26 | 0 | 0
Low Level / Mackintosh Hall | 2012-10-09 | O6-5 |  | 0.007 | clear | 219 | 793 | none | 7.83 | none | 0.12 | 0 | 0
South District / Fire Brigade | 2012-10-16 | O6-7 |  | 0.019 | clear | 223 | 774 | none | 7.66 | none | 0.26 | 0 | 0
Low Level / Central Police Station | 2012-10-16 | O6-8 |  | 0.025 | clear | 222 | 780 | none | 7.34 | none | 0.3 | 0 | 0
North Front / Devils Tower Rd Cemetery | 2012-10-23 | O6-10 |  | nil | clear | 229 | 787 | none | 8.09 | none | 0.37 | 0 | 0
Low Level / Main Street / Piazza Toilets | 2012-10-23 | O6-11 |  | nil | clear | 223 | 787 | none | 8.05 | none | 0.41 | 0 | 0
South District / Fire Brigade | 2012-10-25 | O6-13 |  | 0.109 | clear | 222 | 760 | none | 8.2 | none | 0.36 | 0 | 0
South District / Rosia Dale | 2012-10-30 | O6-14 |  | 0.011 | clear | 211 | 725 | none | 8.17 | none | 0.17 | 0 | 0
Low Level / Governors Parade | 2012-11-03 | N6-1 |  | 0.024 | clear | 232 | 780 | none | 7.92 | none | 0.6 | 0 | 0
North Front / Devils Tower Rd / Car Care | 2012-11-06 | N6-2 |  | nil | clear | 228 | 771 | none | 8.48 | none | 0.2 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-11-06 | N6-3 |  | nil | clear | 226 | 800 | none | 8.04 | none | 0.27 | 0 | 0
Waterport / Gib Elec | 2012-11-15 | N6-5 |  | nil | clear | 227 | 776 | none | 8.45 | none | 0.27 | 0 | 0
Low Level / Watergate House | 2012-11-15 | N6-6 |  | nil | clear | 225 | 771 | none | 8.16 | none | 0.37 | 0 | 0
High Level / Arengos Nursery | 2012-11-20 | N6-8 |  | 0.004 | clear | 234 | 832 | none | 8.25 | none | 0.14 | 0 | 0
Low Level / Gibraltar College | 2012-11-20 | N6-9 |  | 0.002 | clear | 231 | 822 | none | 7.75 | none | 0.36 | 0 | 0
North Front / Devils Tower Rd Cemetery | 2012-11-28 | N6-11 |  | nil | clear | 231 | 811 | none | 8 | none | 0.18 | 0 | 0
Low Level / Central Police Station | 2012-11-28 | N6-12 |  | nil | clear | 227 | 797 | none | 7.92 | none | 0.56 | 0 | 0
Reclamation / Morrisons Superstore | 2012-12-04 | D6-1 |  | nil | clear | 219 | 787 | none | 7.9 | none | 0.12 | 0 | 0
Low Level / I.C.C | 2012-12-04 | D6-2 |  | nil | clear | 222 | 782 | none | 7.86 | none | 0.39 | 0 | 0
Europa District / Highcliff House | 2012-12-04 | D6-3 |  | nil | clear | 224 | 795 | none | 7.89 | none | 0.15 | 0 | 0
South District / Fire Brigade | 2012-12-12 | D6-4 |  | 0.001 | clear | 219 | 781 | none | 7.79 | none | 0.35 | 0 | 0
Low Level / Mackintosh Hall | 2012-12-12 | D6-5 |  | nil | clear | 228 | 796 | none | 7.85 | none | 0.3 | 0 | 0
Europa District / Clifftons | 2012-12-12 | D6-6 |  | nil | clear | 221 | 794 | none | 7.67 | none | 0.16 | 0 | 0
Waterport / Port Authority | 2012-12-17 | D6-7 |  | 0.006 | clear | 225 | 799 | none | 7.82 | none | 0.17 | 0 | 0
Low Level / Main Street / Piazza Toilets | 2012-12-17 | D6-8 |  | 0.002 | clear | 227 | 799 | none | 7.78 | none | 1.61 | 0 | 0
Europa District / Sunset Close | 2012-12-17 | D6-9 |  | 0.001 | clear | 229 | 814 | none | 7.79 | none | 0.17 | 0 | 0
Low Level / Glacis Estate | 2012-12-24 | D6-10 |  | nil | clear | 221 | 796 | none | 7.71 | none | 0.42 | 0 | 0
Low Level / Gibraltar Chronicle | 2012-12-24 | D6-11 |  | nil | clear | 221 | 805 | none | 7.67 | none | 0.29 | 0 | 0
Europa District / Clifftons | 2012-12-24 | D6-12 |  | nil | clear | 217 | 772 | none | 7.63 | none | 0.29 | 0 | 0
Zone1- CEMENTRY | 2013-01-02 | J19-1 |  | 0.001 | clear | 216 | 750 | none | 7.69 | none | 0.29 | 0 | 0
Zone2- CENTRAL POLICE STATION | 2013-01-02 | J19-2 |  | 0.001 | clear | 221 | 769 | none | 7.59 | none | 0.44 | 0 | 0
Zone3- SUNSET CLOSE | 2013-01-02 | J19-3 |  | nil | clear | 220 | 763 | none | 7.66 | none | 0.11 | 0 | 0
Zone1- GIB ELEC POWERSTATION | 2013-01-08 | J19-4 |  | 0.007 | clear | 235 | 820 | none | 7.77 | none | 0.27 | 0 | 0
Zone2- COLLEGE | 2013-01-08 | J19-5 |  | nil | clear | 239 | 826 | none | 7.47 | none | 0.25 | 0 | 0
Zone3- THE CLIFTONS | 2013-01-08 | J19-6 |  | nil | clear | 242 | 850 | none | 7.69 | none | 0.17 | 0 | 0
Zone1- MORRISONS | 2013-01-15 | J19-7 |  | 0.001 | clear | 227 | 805 | none | 7.91 | none | 0.2 | 0 | 0
Zone2- MACKINTOSH HALL | 2013-01-15 | J19-8 |  | NIL | clear | 223 | 813 | none | 7.82 | none | 0.35 | 0 | 0
Zone3- LANCESTER HOUSE | 2013-01-15 | J19-9 |  | NIL | clear | 212 | 770 | Slight chlo | 7.73 | none | 0.15 | 0 | 0
Zone1- FIRESTATION | 2013-01-22 | J19-10 |  | 0.019 | clear | 219 | 754 | none | 8.07 | none | 0.25 | 0 | 0
Zone2- ICC TOILETS | 2013-01-22 | J19-11 |  | 0.016 | clear | 226 | 783 | none | 7.88 | none | 0.5 | 0 | 0
Zone3- SUNSET CLOSE | 2013-01-22 | J19-12 |  | 0.017 | clear | 207 | 712 | none | 7.92 | none | 0.13 | 0 | 0
Zone1- Nelson's View | 29/01/13 | J19-13 |  | 0.004 | clear | 225 | 778 | none | 7.81 | none | 0.2 | 0 | 0
Zone1 - Piazza | 29/01/13 | J19-14 |  | 0 | clear | 221 | 772 | none | 7.78 | none | 0.32 | 0 | 0
Zone3 - Clifftons | 29/01/13 | J19-15 |  | 0 | clear | 247 | 878 | none | 7.76 | none | 0.12 | 0 | 0
Zone1- Arengo's nursery | 2013-02-05 | F7-1 |  | 0.001 | clear | 218 | 786 | none | 8.07 | none | 0.15 | 0 | 0
Zone2- Chronicle | 2013-02-05 | F7-2 |  | nil | clear | 219 | 805 | none | 7.96 | none | 0.25 | 0 | 0
Zone3- Sunset Close | 2013-02-05 | F7-3 |  | 0.002 | clear | 220 | 789 | none | 7.9 | none | 0.1 | 0 | 0
Zone1- Gib Elec | 2013-02-12 | F7-4 |  | nil | clear | 218 | 780 | none | 7.66 | none | 0.89 | 0 | 0
Zone2- Police Station | 2013-02-12 | F7-5 |  | nil | clear | 219 | 788 | none | 7.53 | none | 0.47 | 0 | 0
Zone3- Clifftop | 2013-02-12 | F7-6 |  | nil | clear | 209 | 761 | none | 7.74 | none | 0.26 | 0 | 0
Zone1- Glacis | 2013-02-19 | F7-7 |  | nil | clear | 221 | 801 | none | 7.89 | none | 0.38 | 0 | 0
Zone2- College | 2013-02-19 | F7-8 |  | nil | clear | 219 | 810 | none | 7.62 | none | 0.23 | 0 | 0
Zone3- Lancester | 2013-02-19 | F7-9 |  | nil | clear | 222 | 799 | none | 7.82 | none | 0.19 | 0 | 0
Zone1- Cementry | 2013-02-26 | F7-10 |  | nil | clear | 212 | 737 | none | 7.81 | none | 0.17 | 0 | 0
Zone2- Mackintosh Hall | 2013-02-26 | F7-11 |  | nil | clear | 217 | 759 | none | 7.73 | none | 0.35 | 0 | 0
Zone3- Clifftons | 2013-02-26 | F7-12 |  | nil | clear | 209 | 747 | none | 7.73 | none | 0.32 | 0 | 0
Zone1- Gib Elec Power Station | 2013-03-05 | M13-1 |  | 0.019 | clear | 203 | 716 | none | 8.09 | none | 0.73 | 0 | 0
Zone2- ICC toilets | 2013-03-05 | M13-2 |  | 0.02 | clear | 212 | 738 | none | 7.83 | none | 0.59 | 0 | 0
Zone3- Clifftons | 2013-03-05 | M13-3 |  | 0.019 | clear | 186 | 658 | none | 7.97 | none | 0.21 | 0 | 0
Zone1- Morrisons | 2013-03-13 | M13-4 |  | 0.033 | clear | 201 | 730 | none | 7.94 | none | 0.39 | 0 | 0
Zone2- Piazza | 2013-03-13 | M13-5 |  | 0.032 | clear | 205 | 722 | none | 7.82 | none | 0.7 | 0 | 0
Zone3- Sunset Close | 2013-03-13 | M13-6 |  | 0.041 | clear | 222 | 781 | none | 7.94 | none | 0.55 | 0 | 0
Zone1- Firestation | 2013-03-20 | M13-7 |  | 0.062 | clear | 216 | 754 | none | 8.1 | none | 0.16 | 0 | 0
Zone2- Chronicle | 2013-03-20 | M13-8 |  | 0.059 | clear | 212 | 730 | none | 8.01 | none | 0.4 | 0 | 0
Zone3- Lancaster House | 2013-03-20 | M13-9 |  | 0.046 | clear | 233 | 819 | none | 7.97 | none | 0.21 | 0 | 0
Zone1- Sacred Heart | 2013-03-26 | M13-10 |  | 0.052 | clear | 214 | 741 | none | 8.06 | none | 0.45 | 0 | 0
Zone2- Gibraltar Regiment cafe | 2013-03-26 | M13-11 |  | 0.041 | clear | 215 | 739 | none | 7.78 | none | 0.38 | 0 | 0
Zone3- Clifftons | 2013-03-26 | M13-12 |  | 0.038 | clear | 209 | 743 | none | 8.11 | none | 0.4 | 0 | 0
Zone1- Arengos Nursery | 2013-04-03 | A13-1 |  | 0.021 | clear | 210 | 732 | none | 7.95 | none | 0.23 | 0 | 0
Zone2- John Mackintosh Hall | 2013-04-03 | A13-2 |  | 0.024 | clear | 212 | 750 | none | 8.12 | none | 0.43 | 0 | 0
Zone3- Clifftop | 2013-04-03 | A13-3 |  | 0.024 | clear | 208 | 735 | none | 8.1 | none | 0.58 | 0 | 0
Zone1- Victoria Stadium | 2013-04-09 | A13-4 |  | 0.019 | clear | 195 | 693 | none | 8.41 | none | 0.16 | 0 | 0
Zone2- Casemates | 2013-04-09 | A13-5 |  | 0.019 | clear | 211 | 748 | none | 8.28 | none | 0.31 | 0 | 0
Zone3- Sunset Close | 2013-04-09 | A13-6 |  | 0.019 | clear | 183 | 597 | none | 8.3 | none | 0.13 | 0 | 0
Zone1- Firestation | 2013-04-16 | A13-7 |  | 0.019 | clear | 207 | 739 | none | 8.08 | none | 0.73 | 0 | 0
Zone2- Chronicle | 2013-04-16 | A13-8 |  | 0.018 | clear | 211 | 746 | none | 8.16 | none | 0.37 | 0 | 0
Zone3- Lancaster House | 2013-04-16 | A13-9 |  | 0.018 | clear | 232 | 832 | none | 7.98 | none | 0.17 | 0 | 0
Zone1- Cementary road (Paint Shop) | 2013-04-23 | A13-10 |  | 0.0023 | clear | 217 | 755 | none | 8.4 | none | 0.54 | 0 | 0
Zone2- Bristol Hotel | 2013-04-23 | A13-11 |  | 0.027 | clear | 209 | 743 | none | 8.14 | none | 0.79 | 0 | 0
Zone3- Sunset Close | 2013-04-23 | A13-12 |  | 0.026 | clear | 215 | 777 | none | 8.51 | none | 0.12 | 0 | 0
Zone1 - Gib Oil, Waterport | 2013-07-04 | J21-1 |  | 0.018 | clear | 224 | 796 | none | 8.27 | none | 8.27 | 0 | 0
Zone2-LL-Eng Lane Bean / Gone Cafe | 2013-07-02 | J21-2 |  | 0.018 | clear | 212 | 712 | none | 6.68 | none | 6.68 | 0 | 0
Zone3-ED-Lathbury Barracks | 2013-07-02 | J21-3 |  | 0.02 | clear | 255 | 831 | none | 7.55 | none | 7.55 | 0 | 0
Zone1 - St Bernards Hospital | 2013-07-09 | J21-4 |  | 0.014 | clear | 220 | 776 | none | 8.22 | none | 8.22 | 0 | 0
Zone2-LL- Cheers, Cornwalls Parade | 2013-07-09 | J21-5 |  | 0.017 | clear | 217 | 775 | none | 8.02 | none | 8.02 | 0 | 0
Zone3-ED- Lancashire House | 2013-07-09 | J21-6 |  | 0.015 | clear | 264 | 926 | none | 7.9 | none | 7.9 | 0 | 0
Zone1 - Caleta Hotel | 2013-07-16 | J21-7 |  | 0.021 | clear | 213 | 760 | none | 8.11 | none | 8.11 | 0 | 0
Zone2-LL- Leisure Centre | 2013-07-16 | J21-8 |  | 0.021 | clear | 218 | 754 | none | 8.03 | none | 8.03 | 0 | 0
Zone3-ED- Sunset Close | 2013-07-16 | J21-9 |  | 0.019 | clear | 211 | 738 | none | 8.21 | none | 8.21 | 0 | 0
Zone1 - Varyl Begg Estate | 2013-07-25 | J21-10 |  | 0.02 | clear | 210 | 749 | none | 8.03 | none | 8.03 | 0 | 0
Zone2-LL- The Bristol Hotel | 2013-07-25 | J21-11 |  | 0.018 | clear | 213 | 753 | none | 8.08 | none | 8.08 | 0 | 0
Zone3-ED- Victoria Tower, Byrmpton | 2013-07-25 | J21-12 |  | 0.018 | clear | 195 | 690 | none | 8.05 | none | 8.05 | 0 | 0
Zone1 - Gibtelecom, New Harbours | 2013-07-30 | A14-1 |  | 0.022 | clear | 192 | 702 | none | 8.1 | none | 0.2 | 0 | 0
Zone2-LL- Duke of Kent House | 2013-07-30 | A14-2 |  | 0.021 | clear | 211 | 746 | none | 7.8 | none | 0.3 | 0 | 0
Zone3-ED- Clifftons | 2013-07-30 | A14-3 |  | 0.023 | clear | 194 | 700 | none | 8.01 | none | 0.1 | 0 | 0
Zone1 - Montagu Gardens | 2013-08-06 | A14-4 |  | 0.017 | clear | 218 | 776 | none | 7.72 | none | 0.3 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2013-08-08 | A14-5 |  | 0.022 | clear | 211 | 763 | none | 7.59 | none | 0.4 | 0 | 0
Zone3-ED- Lathbury Barracks | 2013-08-06 | A14-6 |  | 0.02 | clear | 234 | 836 | none | 7.54 | none | 0.2 | 0 | 0
Zone1 - Victoria Stadium | 2013-08-13 | A14-7 |  | 0.027 | clear | 212 | 767 | none | 7.42 | none | 0.1 | 0 | 0
Zone2-LL- ICC | 2013-08-13 | A14-8 |  | 0.021 | clear | 211 | 765 | none | 7.58 | none | 0.2 | 0 | 0
Zone3-ED- Lancashire House | 2013-08-13 | A14-9 |  | 0.021 | clear | 246 | 884 | none | 7.61 | none | 0.3 | 0 | 0
Zone1 - R13 High Level, Tank Ramp | 2013-08-20 | A14-10 |  | 0.015 | clear | 200 | 734 | none | 7.56 | none | 0.3 | 0 | 0
Zone2-LL- R12, Road to Lines | 2013-08-20 | A14-11 |  | 0.018 | clear | 212 | 781 | none | 7.52 | none | 0.3 | 0 | 0
Zone3-ED- Sunset Close | 2013-08-20 | A14-12 |  | 0.017 | clear | 195 | 724 | none | 7.87 | none | 0.2 | 0 | 0
Zone1 - Tankerville House, MC Estate | 2013-08-28 | A14-13 |  | 0.014 | clear | 231 | 832 | none | 7.42 | none | 0.5 | 0 | 0
Zone2-LL-Aragon Bar, Bell Lane | 2013-08-28 | A14-14 |  | 0.026 | clear | 215 | 790 | none | 7.63 | none | 0.3 | 0 | 0
Zone3-ED- Loreto Nursery | 2013-08-28 | A14-15 |  | 0.016 | clear | 257 | 911 | none | 7.6 | none | 0.3 | 0 | 0
Zone1 - Shipping, Gib Elec | 2013-09-03 | S7-1 |  | 0.016 | clear | 225 | 807 | none | 7.94 | none | 0.31 | 0 | 0
Zone2-LL- Engineer's Lane | 2013-09-03 | S7-2 |  | 0.018 | clear | 220 | 794 | none | 7.71 | none | 0.33 | 0 | 0
Zone3-ED- Clifftons | 2013-09-03 | S7-3 |  | 0.015 | clear | 227 | 830 | none | 7.86 | none | 0.24 | 0 | 0
Zone1 - Kingsway House, Alameda Estate | 2013-09-11 | S7-4 |  | 0.091 | clear | 222 | 779 | none | 8.09 | none | 0.36 | 0 | 0
Zone2-LL- Bristol Hotel | 2013-09-11 | S7-5 |  | 0.086 | clear | 222 | 777 | none | 7.84 | none | 0.43 | 0 | 0
Zone3-ED- Lathbury Industrial Park | 2013-09-11 | S7-6 |  | 0.09 | clear | 247 | 880 | none | 7.79 | none | 0.31 | 0 | 0
Zone1 - North Front, Blands, Bayside Road | 2013-09-19 | S7-7 |  | nil | clear | 212 | 777 | none | 7.96 | none | 0.25 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2013-09-19 | S7-8 |  | 0.01 | clear | 212 | 773 | none | 7.64 | none | 0.27 | 0 | 0
Zone3-ED- Clifftop | 2013-09-19 | S7-9 |  | 0.01 | clear | 213 | 780 | none | 7.67 | none | 0.47 | 0 | 0
Zone1 - AquaGib main office, Leanse Place | 2013-09-24 | S7-10 |  | 0.018 | clear | 220 | 798 | none | 8.09 | none | 0.21 | 0 | 0
Zone2-LL- Gib Chronicle, Casemates Square | 2013-09-24 | S7-11 |  | 0.019 | clear | 214 | 756 | none | 8.02 | none | 0.33 | 0 | 0
Zone3-ED- Loreto Convent Nursery, Mount | 2013-09-24 | S7-12 |  | 0.019 | clear | 245 | 873 | none | 7.74 | none | 0.4 | 0 | 0
Zone1 - St Bernard's Hospital | 2013-10-01 | O7-1 |  | 0.015 | clear | 217 | 771 | none | 7.94 | none | 0.21 | 0 | 0
Zone2-LL- MRW, Cornwall's Parade | 2013-10-01 | O7-2 |  | 0.015 | clear | 217 | 766 | none | 7.8 | none | 0.38 | 0 | 0
Zone3-ED- Clifftons | 2013-10-01 | O7-3 |  | 0.018 | clear | 203 | 742 | none | 7.69 | none | 0.23 | 0 | 0
Zone1 - Kingsway House, Alameda Estate | 2013-10-09 | O7-4 |  | 0.045 | clear | 207 | 751 | none | 7.98 | none | 1.16 | 0 | 0
Zone2-LL- Bristol Hotel | 2013-10-09 | O7-5 |  | 0.026 | clear | 207 | 725 | none | 7.86 | none | 1.62 | 0 | 0
Zone3-ED- Sunset Close | 2013-10-09 | O7-6 |  | 0.022 | clear | 195 | 708 | none | 7.88 | none | 0.24 | 0 | 0
Zone1 - Shipping, Gib Elec | 2013-10-18 | O7-7 |  | 0.02 | clear | 207 | 736 | none | 8 | none | 0.31 | 0 | 0
Zone2-LL- ICC | 2013-10-15 | O7-8 |  | 0.007 | clear | 201 | 722 | none | 7.54 | none | 0.36 | 0 | 0
Zone3-ED- Clifftop | 2013-10-18 | O7-9 |  | 0.021 | clear | 200 | 716 | none | 7.8 | none | 0.32 | 0 | 0
Zone1 - AquaGib, Ragged Staff | 2013-10-22 | O7-10 |  | 0.014 | clear | 212 | 766 | none | 7.81 | none | 0.25 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2013-10-22 | O7-11 |  | 0.014 | clear | 207 | 734 | none | 7.71 | none | 0.48 | 0 | 0
Zone 3 - Sunset Close | 2013-10-24 | O7-12 |  | 0.019 | clear | 202 | 713 | none | 7.83 | none | 0.34 | 0 | 0
Zone1 - North Front, Cementary Road | 2013-10-22 | O7-13 |  | 0.015 | clear | 202 | 722 | none | 7.96 | none | 0.24 | 0 | 0
Zone2-LL- Governor's Street | 2013-10-22 | O7-14 |  | 0.018 | clear | 204 | 737 | none | 7.95 | none | 0.43 | 0 | 0
Zone 3 - Clifftons | 2013-10-24 | O7-15 |  | 0.014 | clear | 217 | 698 | none | 7.85 | none | 0.29 | 0 | 0
Zone1 - 6 Library Ramp | 2013-11-05 | N4-1 |  | 0.016 | clear | 212 | 750 | none | 8.25 | none | 0.33 | 0 | 0
Zone2-LL- Engineer's Lane | 2013-11-05 | N4-2 |  | 0.017 | clear | 209 | 746 | none | 8.1 | none | 0.38 | 0 | 0
Zone3-ED- Clifton Mews | 2013-11-05 | N4-3 |  | 0.018 | clear | 202 | 732 | none | 8.13 | none | 0.28 | 0 | 0
Zone1 - St Bernard's Hospital | 2013-11-11 | N4-4 |  | 0.016 | clear | 197 | 717 | none | 8.09 | none | 0.33 | 0 | 0
Zone2-LL- Bristol Hotel | 2013-11-11 | N4-5 |  | 0.018 | clear | 209 | 736 | none | 8.1 | none | 0.36 | 0 | 0
Zone3-ED- Sunset Close | 2013-11-11 | N4-6 |  | 0.016 | clear | 179 | 640 | none | 8.14 | none | 0.23 | 0 | 0
Zone1 - Caleta Hotel | 2013-11-18 | N4-7 |  | 0.023 | clear | 194 | 621 | none | 8.09 | none | 0.28 | 0 | 0
Zone2-LL- Kings Bastion, Leisure Centre | 2013-11-20 | N4-8 |  | 0.018 | clear | 207 | 730 | none | 8.08 | none | 0.46 | 0 | 0
Zone3-ED- Clifton Mews | 2013-11-18 | N4-9 |  | 0.023 | clear | 205 | 682 | none | 7.87 | none | 0.63 | 0 | 0
Zone1 - Moorish Castle Estate | 2013-11-27 | N4-10 |  | 0.013 | clear | 213 | 756 | none | 8.28 | none | 0.37 | 0 | 0
Zone2-LL- Casemates | 2013-11-27 | N4-11 |  | 0.016 | clear | 214 | 754 | none | 8.19 | none | 0.85 | 0 | 0
Zone3-ED- Highcliffe House | 2013-11-27 | N4-12 |  | 0.015 | clear | 210 | 741 | none | 8.19 | none | 0.43 | 0 | 0
Zone1 - Shipping, Gib Elec | 2013-12-02 | D7-1 |  | 0.017 | clear | 212 | 746 | none | 8.46 | none | 0.53 | 0 | 0
Zone2-LL- Line Wall Road, Gib Oil | 2013-12-02 | D7-2 |  | 0.017 | clear | 211 | 732 | none | 8.58 | none | 0.45 | 0 | 0
Zone3-ED- Sunset Close | 2013-12-02 | D7-3 |  | 0.016 | clear | 194 | 695 | none | 8.52 | none | 0.31 | 0 | 0
Zone 1 - South District, Rosia House | 2013-12-09 | D7-4 |  | 0.016 | clear | 214 | 755 | none | 8.41 | none | 0.33 | 0 | 0
Zone 2 - Secretary's Lane, Group 5 | 2013-12-09 | D7-5 |  | 0.017 | clear | 216 | 752 | none | 8.34 | none | 0.77 | 0 | 0
Zone 3 - Cliffton Mews | 2013-12-09 | D7-6 |  | 0.016 | clear | 197 | 700 | none | 8.21 | none | 0.38 | 0 | 0
Zone 1 - North Front, Laguna Estate | 2013-12-16 | D7-7 |  | 0.017 | clear | 225 | 777 | none | 8.49 | none | 0.44 | 0 | 0
Zone 2 - Gavino's Passage | 2013-12-16 | D7-8 |  | 0.019 | clear | 218 | 761 | none | 8.31 | none | 0.65 | 0 | 0
Zone 3 - Clifftons | 2013-12-16 | D7-9 |  | 0.021 | clear | 210 | 745 | none | 8.25 | none | 0.6 | 0 | 0
Zone 1 - High Level, Tank Ramp | 2013-12-22 | D7-10 |  | 0.016 | clear | 212 | 732 | none | 8.38 | none | 0.43 | 0 | 0
Zone 2 - Engineer's Lane, Continental Hotel | 2013-12-22 | D7-11 |  | 0.016 | clear | 217 | 759 | none | 8.3 | none | 0.48 | 0 | 0
Zone 3 - Sunset Close | 2013-12-22 | D7-12 |  | 0.017 | clear | 192 | 680 | none | 8.26 | none | 0.52 | 0 | 0
Zone 1 - Westside, St Bernard's Hospital | 2014-01-02 | D7-13 |  | 0.012 | clear | 206 | 748 | none | 8.05 | none | 0.47 | 0 | 0
Zone 2 - The Chronicle, Casemates | 2014-01-02 | D7-14 |  | 0.015 | clear | 215 | 761 | none | 8.05 | none | 1.15 | 0 | 0
Zone 3 - Cliffton Mews | 2013-12-30 | D7-15 |  | 0.013 | clear | 180 | 661 | none | 7.67 | none | 0.38 | 0 | 0
Zone1 - Keightley House, Moorish Castle Est | 2014-01-06 | J22-1 |  | 0.013 | clear | 209 | 739 | none | 8.27 | none | 0.38 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2014-01-06 | J22-2 |  | 0.042 | clear | 212 | 756 | none | 8 | none | 0.77 | 0 | 0
Zone3-ED- Highcliffe House | 2014-01-06 | J22-3 |  | 0.056 | clear | 210 | 731 | none | 8.09 | none | 0.32 | 0 | 0
Zone 1 - Shipping distribution, Gib Elec | 2014-01-13 | J22-4 |  | 0.019 | clear | 213 | 775 | none | 8.3 | none | 0.47 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-01-13 | J22-5 |  | 0.019 | clear | 210 | 758 | none | 8.16 | none | 0.49 | 0 | 0
Zone 3 - Sunset Close | 2014-01-13 | J22-6 |  | 0.02 | clear | 185 | 662 | none | 8.15 | none | 0.39 | 0 | 0
Zone 1 - S District,Gibtelecom, New Harbours | 2014-01-20 | J22-7 |  | 0.002 | clear | 201 | 699 | none | 8.26 | none | 0.29 | 0 | 0
Zone 2 - Piaza | 2014-01-20 | J22-8 |  | 0.002 | clear | 207 | 753 | none | 8.09 | none | 1.03 | 0 | 0
Zone 3 - The Cliftons | 2014-01-20 | J22-9 |  | 0.002 | clear | 169 | 826 | none | 8.14 | none | 0.29 | 0 | 0
Zone 1 - High Level, Tank Ramp | 2014-01-27 | J22-10 |  | 0.017 | clear | 215 | 761 | none | 8.22 | none | 0.27 | 0 | 0
Zone 2 - Engineer's Lane, Continental Hotel | 2014-01-27 | J22-11 |  | 0.019 | clear | 207 | 746 | none | 8.4 | none | 0.6 | 0 | 0
Zone 3 - Sunset Close | 2014-01-27 | J22-12 |  | 0.017 | clear | 198 | 731 | none | 8.37 | none | 0.25 | 0 | 0
Zone1 - High Level, Sacred Heart School | 2014-02-03 | F8-1 |  | 0.016 | clear | 222 | 787 | none | 8.19 | none | 0.36 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2014-02-05 | F8-2 |  | 0.017 | clear | 215 | 763 | none | 8.07 | none | 0.51 | 0 | 0
Zone3-ED- Sunset Close | 2014-02-03 | F8-3 |  | 0.015 | clear | 236 | 842 | none | 8.24 | none | 0.39 | 0 | 0
Zone 1 - Westside, Morrisons | 2014-02-10 | F8-4 |  | 0.012 | clear | 212 | 856 | none | 7.14 | none | 0.33 | 0 | 0
Zone 2 - Gavinos Passage | 2014-02-10 | F8-5 |  | 0.013 | clear | 218 | 759 | none | 8.18 | none | 0.49 | 0 | 0
Zone 3 - Clifton Mews | 2014-02-10 | F8-6 |  | 0.013 | clear | 192 | 674 | none | 8.21 | none | 0.3 | 0 | 0
Zone 1 - Moorish Castle Estate shop | 2014-02-17 | F8-7 |  | 0.011 | clear | 227 | 793 | none | 8.22 | none | 0.35 | 0 | 0
Zone 2 - Casemates | 2014-02-17 | F8-8 |  | 0.012 | clear | 221 | 780 | none | 8.18 | none | 0.56 | 0 | 0
Zone 3 - Highcliffe House | 2014-02-17 | F8-9 |  | 0.012 | clear | 217 | 748 | none | 8.16 | none | 0.32 | 0 | 0
Zone 1 - Shipping, Aquagib, Distiller | 2014-02-24 | F8-10 |  | 0.016 | clear | 247 | 868 | none | 8.22 | none | 0.35 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-02-24 | F8-11 |  | 0.016 | clear | 237 | 782 | none | 8.18 | none | 0.37 | 0 | 0
Zone 3 - Sunset Close | 2014-02-24 | F8-12 |  | 0.016 | clear | 244 | 924 | none | 8.18 | none | 0.35 | 0 | 0
Zone1 - South District, 12 Rosia House | 2014-03-06 | M15-1 |  | 0.114 | clear | 202 | 731 | none | 7.96 | none | 0.25 | 0 | 0
Zone2-LL- Gib Chroncile, Casemates | 2014-03-06 | M15-2 |  | 0.086 | clear | 220 | 786 | none | 7.93 | none | 0.43 | 0 | 0
Zone3-ED- Cliffton Mews | 2014-03-06 | M15-3 |  | 0.06 | clear | 198 | 716 | none | 7.85 | none | 0.26 | 0 | 0
Zone 1 - North Front, Oak Garage, Devils Tower Road | 2014-03-12 | M15-4 |  | 0.025 | clear | 198 | 703 | none | 7.97 | none | 0.34 | 0 | 0
Zone 2 - Kings Bastion Leisure Centre | 2014-03-12 | M15-5 |  | 0.027 | clear | 217 | 776 | none | 7.8 | none | 0.35 | 0 | 0
Zone 3 - Highcliffe House | 2014-03-12 | M15-6 |  | 0.038 | clear | 211 | 738 | none | 8 | none | 0.29 | 0 | 0
Zone 1 - High Level, Arengo's Nursery | 2014-03-18 | M15-7 |  | 0.003 | clear | 212 | 784 | none | 8.25 | none | 0.35 | 0 | 0
Zone 2 - Piazza | 2014-03-18 | M15-8 |  | 0.005 | clear | 212 | 771 | none | 8.19 | none | 0.82 | 0 | 0
Zone 3 - Sunset Close | 2014-03-20 | M15-9 |  | 0.003 | clear | 211 | 759 | none | 8.01 | none | 0.33 | 0 | 0
Zone 1 - Westside, Morrisons | 2014-03-25 | M15-10 |  | nil | clear | 214 | 767 | none | 8.06 | none | 0.32 | 0 | 0
Zone 2 - Casemates | 2014-03-25 | M15-11 |  | 0.003 | clear | 215 | 766 | none | 8.21 | none | 0.3 | 0 | 0
Zone3-ED- Cliffton Mews | 2014-03-25 | M15-12 |  | nil | clear | 202 | 738 | none | 8.29 | none | 0.25 | 0 | 0
Zone1 -Moorish Castle Estate-Anderson Hse | 2014-04-01 | DA15-1 |  | <0.009 | clear | 222 | 776 | none | 8.27 | none | 0.58 | 0 | 0
Zone2-Low Level-John Mackintosh Hall | 2014-04-01 | DA15-2 |  | <0.009 | clear | 207 | 740 | none | 8.25 | none | 0.48 | 0 | 0
Zone3-Europa District-Cliffton Mews | 2014-04-01 | DA15-3 |  | 0.012 | clear | 230 | 815 | none | 8.34 | none | 0.58 | 0 | 0
Zone 1 - Shipping district, Gib Elec | 2014-04-07 | DA15-4 |  | <0.009 | clear | 220 | 767 | none | 8.25 | none | 0.33 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-04-07 | DA15-5 |  | <0.009 | clear | 221 | 800 | none | 8.25 | none | 0.47 | 0 | 0
Zone 3 - Sunset Close | 2014-04-09 | DA15-6 |  | <0.009 | clear | 197 | 790 | none | 8.03 | none | 0.42 | 0 | 0
Zone 1 - Shipping, Distiller, AquaGib | 2014-04-14 | DA15-7 |  | <0.009 | clear | 214 | 758 | none | 8.36 | none | 0.43 | 0 | 0
Zone 2 - Gib Chronicle, Line Wall Road | 2014-04-14 | DA15-8 |  | <0.009 | clear | 216 | 771 | none | 8.31 | none | 0.47 | 0 | 0
Zone3-ED- Cliffton Mews | 2014-04-14 | DA15-9 |  | <0.009 | clear | 192 | 694 | none | 8.27 | none | 0.4 | 0 | 0
Zone 1 - North Front, Victoria Stadium | 2014-04-22 | DA15-10 |  | <0.009 | clear | 238 | 760 | none | 9.09 | none | 0.34 | 0 | 0
Zone 2 - Casemates | 2014-04-22 | DA15-11 |  | <0.009 | clear | 222 | 760 | none | 8.26 | none | 0.49 | 0 | 0
Zone 3 - Highcliffe | 2014-04-22 | DA15-12 |  | <0.009 | clear | 245 | 850 | none | 8.07 | none | 0.35 | 0 | 0
Zone1 - High Level, Arengo's Nursery | 2014-04-29 | DM16-1 |  | <0.009 | clear | 209 | 760 | none | 7.93 | none | 0.11 | 0 | 0
Zone2-LL- John Mackintosh Square | 2014-04-29 | DM16-2 |  | <0.009 | clear | 216 | 776 | none | 7.73 | none | 0.21 | 0 | 0
Zone 3 - Sunset Close | 2014-04-29 | DM16-3 |  | <0.009 | clear | 198 | 731 | none | 7.91 | none | 0.18 | 0 | 0
Zone 1 - Westside, Harbour Views | 2014-05-07 | DM16-4 |  | <0.009 | clear | 206 | 717 | none | 8.3 | none | 0.21 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-05-07 | DM16-5 |  | <0.009 | clear | 212 | 736 | none | 8.29 | none | 0.22 | 0 | 0
Zone3-ED- Cliffton Mews | 2014-05-05 | DM16-6 |  | <0.009 | clear | 200 | 763 | none | 8.22 | none | 0.18 | 0 | 0
Zone 1 - Aquagib, Ragged Staff | 2014-05-15 | DM16-7 |  | <0.009 | clear | 219 | 756 | none | 8.28 | none | 0.25 | 0 | 0
Zone 2 - Kings Bastion Leisure Centre | 2014-05-15 | DM16-8 |  | <0.009 | clear | 228 | 755 | none | 8.28 | none | 0.29 | 0 | 0
Zone3-ED- Sunset Close | 2014-05-15 | DM16-9 |  | <0.009 | clear | 224 | 743 | none | 8.28 | none | 0.23 | 0 | 0
Zone 1 - High Level, Arengo's Nursery | 2014-05-22 | DM16-10 |  | <0.009 | clear | 223 | 802 | none | 8.25 | none | 0.17 | 0 | 0
Zone2-LL- John Mackintosh Square | 2014-05-22 | DM16-11 |  | <0.009 | clear | 221 | 806 | none | 8.14 | none | 0.15 | 0 | 0
Zone3-ED- Sunset Close | 2014-05-22 | DM16-12 |  | <0.009 | clear | 219 | 777 | none | 8.27 | none | 0.34 | 0 | 0
Zone1 - North Front, Victoria Stadium | 2014-06-02 | D J23-1 |  | <0.009 | clear | 210 | 774 | none | 7.67 | none | 0.55 | 0 | 0
Zone2-LL- John Mackintosh Square | 2014-06-02 | D J23-2 |  | <0.009 | clear | 217 | 789 | none | 7.79 | none | 0.38 | 0 | 0
Zone3-ED- The Clifftons | 2014-06-02 | D J23-3 |  | <0.009 | clear | 201 | 744 | none | 7.83 | none | 0.19 | 0 | 0
Zone 1 - Shipping distribution, Gib Elec | 2014-06-09 | D J23-4 |  | <0.009 | clear | 220 | 791 | none | 8.17 | none | 0.1 | 0 | 0
Zone 2 - Kings Bastion Leisure Centre | 2014-06-09 | D J23-5 |  | <0.009 | clear | 213 | 787 | none | 8.15 | none | 0.24 | 0 | 0
Zone 3 - Sunset Close | 2014-06-09 | D J23-6 |  | <0.009 | clear | 204 | 749 | none | 8.1 | none | 0.16 | 0 | 0
Zone 1 - South District, Ragged Staff, Aquagib | 2014-06-17 | D J23-4 |  | <0.009 | clear | 225 | 836 | none | 7.89 | none | 0.4 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-06-17 | D J23-5 |  | <0.009 | clear | 231 | 818 | none | 7.54 | none | 0.2 | 0 | 0
Zone 3 - The clifftons | 2014-06-17 | D J23-6 |  | <0.009 | clear | 208 | 782 | none | 7.75 | none | 0.16 | 0 | 0
Zone 1 - Westside area, Varyl Begg Est | 2014-06-23 | D J23-10 |  | <0.009 | clear | 243 | 828 | none | 7.35 | none | 0.18 | 0 | 0
Zone 2 - The Gibraltar Chronicle | 2014-06-23 | D J23-11 |  | <0.009 | clear | 220 | 829 | none | 8.25 | none | 0.21 | 0 | 0
Zone 3 - Highcliff House | 2014-06-23 | D J23-12 |  | <0.009 | clear | 212 | 792 | none | 8.2 | none | 0.07 | 0 | 0
Zone1 - Tankerville House, Moorish Castle | 2014-07-02 | DJ24-1 |  | <0.009 | clear | 206 | 764 | none | 7.96 | none | 0.2 | 0 | 0
Zone2-LL- ICC | 2014-07-02 | DJ24-2 |  | <0.009 | clear | 215 | 788 | none | 7.8 | none | 0.39 | 0 | 0
Zone3-ED- Sunset Close | 2014-07-02 | DJ24-3 |  | <0.009 | clear | 183 | 694 | none | 7.85 | none | 0.13 | 0 | 0
Zone 1 - North Front, Tercentenary stadium | 2014-07-07 | DJ24-4 |  | <0.009 | clear | 202 | 709 | none | 8.07 | none | 0.21 | 0 | 0
Zone 2 - Casemates | 2014-07-07 | DJ24-5 |  | <0.009 | clear | 208 | 785 | none | 7.84 | none | 0.9 | 0 | 0
Zone 3 - The Cliftons | 2014-07-07 | DJ24-6 |  | <0.009 | clear | 185 | 708 | none | 7.98 | none | 0.1 | 0 | 0
Zone 1 - South District, Vineyards | 2014-07-14 | DJ24-7 |  | 0.018 | clear | 216 | 786 | none | 7.82 | none | 0.08 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-07-14 | DJ24-8 |  | 0.012 | clear | 215 | 797 | none | 7.64 | none | 0.22 | 0 | 0
Zone 3 - Highcliffe | 2014-07-14 | DJ24-9 |  | 0.01 | clear | 216 | 809 | none | 8.04 | none | 0.17 | 0 | 0
Zone 1 - Shipping, Distiller | 2014-07-21 | DJ24-10 |  | 0.018 | clear | 216 | 786 | none | 7.82 | none | 0.08 | 0 | 0
Zone 2 - Piazza | 2014-07-21 | DJ24-11 |  | 0.012 | clear | 215 | 797 | none | 7.64 | none | 0.22 | 0 | 0
Zone 3 - Sunset Close | 2014-07-21 | DJ24-12 |  | 0.01 | clear | 216 | 809 | none | 8.04 | none | 0.17 | 0 | 0
Zone1 - Westside, Montagu Gardens | 2014-07-28 | DJ24-13 |  | <0.009 | clear | 218 | 782 | none | 7.8 | none | 0.3 | 0 | 0
Zone 2- King's Bastion | 2014-07-28 | DJ24-14 |  | <0.009 | clear | 183 | 875 | none | 7.88 | none | 0.24 | 0 | 0
Zone 3- Clifftons | 2014-07-28 | DJ24-15 |  | <0.009 | clear | 205 | 749 | none | 7.89 | none | 0.27 | 0 | 0
Upper Rock - Pocca Rocca | 2014-07-30 | URA11-1 |  | <0.009 | clear | 205 | 758 | none | 7.86 | none | 0.19 | 0 | 0
Upper Rock - Devil's Gap | 2014-08-04 | URA11-2 |  | <0.009 | clear | 210 | 778 | none | 7.97 | none | 0.15 | 0 | 0
Zone 1 - Moorish Castle, Balloons II | 2014-08-06 | DA16-4 |  | <0.009 | clear | 209 | 783 | none | 8.25 | none | 0.24 | 0 | 0
Zone 2 - The Chronicle, Casemates | 2014-08-06 | DA16-5 |  | <0.009 | clear | 219 | 812 | none | 8.19 | none | 0.22 | 0 | 0
Zone 3 - Sunset Close | 2014-08-06 | DA16-6 |  | <0.009 | clear | 210 | 785 | none | 8.15 | none | 0.11 | 0 | 0
Zone 1 - North Front, Village Inn Caleta | 2014-08-11 | DA16-7 |  | <0.009 | clear | 220 | 828 | none | 8.21 | none | 0.36 | 0 | 0
Zone 2 - ICC | 2014-08-11 | DA16-8 |  | <0.009 | clear | 219 | 811 | none | 8.17 | none | 0.28 | 0 | 0
Zone 3 - Highcliffe | 2014-08-11 | DA16-9 |  | <0.009 | clear | 221 | 813 | none | 8.14 | none | 0.12 | 0 | 0
Upper Rock - Pocca Rocca | 2014-08-13 | URA11-3 |  | <0.009 | clear | 212 | 804 | none | 8.01 | none | 0.28 | 0 | 0
Zone 1 - Shipping, Distiller, AquaGib | 2014-08-20 | DA16-10 |  | <0.009 | clear | 211 | 797 | none | 7.9 | none | 0.22 | 0 | 0
Zone 2 - Piazza | 2014-08-20 | DA16-11 |  | <0.009 | clear | 218 | 818 | none | 7.92 | none | 0.16 | 0 | 0
Zone 3 - Clifftons | 2014-08-20 | DA16-12 |  | <0.009 | clear | 222 | 824 | none | 7.78 | none | 0.21 | 0 | 0
Upper Rock - Galleries | 2014-08-20 | URA11-4 |  | <0.009 | clear | 198 | 761 | none | 8.01 | none | 0.16 | 0 | 0
Upper Rock - Moorish Castle Tourist Site | 2014-08-26 | URA11-5 |  | <0.009 | clear | 218 | 804 | none | 7.88 | none | 0.14 | 0 | 0
Zone 1 - Ragged Staff | 2014-08-27 | DA16-13 |  | <0.009 | clear | 215 | 795 | none | 7.45 | none | 0.24 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-08-27 | DA16-14 |  | <0.009 | clear | 210 | 793 | none | 7.53 | none | 0.25 | 0 | 0
Zone 3 - Clifftons | 2014-08-27 | DA16-15 |  | <0.009 | clear | 197 | 761 | none | 7.44 | none | 0.06 | 0 | 0
Zone1 - South District, Ragged Staff | 2014-09-29 | DO8-1 |  | <0.009 | clear | 192 | 710 | none | 8.33 | none | 0.1 | 0 | 0
Zone2-LL- Casemates | 2014-09-29 | DO8-2 |  | <0.009 | clear | 207 | 750 | none | 8.14 | none | 0.42 | 0 | 0
Zone3-ED- Highcliffe House | 2014-10-01 | DO8-3 |  | <0.009 | clear | 198 | 701 | none | 8.23 | none | 0.08 | 0 | 0
Devil's Gap | 2014-10-01 | URO5-1 |  | <0.009 | clear | 213 | 713 | none | 8.24 | none | 0.06 | 0 | 0
Zone1 - Westside, St Bernard's Hospital | 2014-10-06 | DO8-4 |  | <0.009 | clear | 206 | 728 | none | 8.1 | none | 0.09 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2014-10-06 | DO8-5 |  | <0.009 | clear | 202 | 754 | none | 8.12 | none | 0.29 | 0 | 0
Zone3-ED- Clifton Mews | 2014-10-06 | DO8-6 |  | <0.009 | clear | 209 | 765 | none | 8.18 | none | 0.12 | 0 | 0
Poca Rocca | 2014-10-06 | URO5-2 |  | <0.009 | clear | 219 | 761 | none | 8.18 | none | 0.12 | 0 | 0
Zone1 - Moorish Castle, 6/1/2 Castle Road | 2014-10-14 | DO8-7 |  | <0.009 | clear | 203 | 750 | none | 8.2 | none | 0.13 | 0 | 0
Zone2-LL- Line Wall Road, Gib Oil | 2014-10-13 | DO8-8 |  | <0.009 | clear | 202 | 746 | none | 8.11 | none | 0.31 | 0 | 0
Zone3-ED- Highcliffe House | 2014-10-14 | DO8-9 |  | <0.009 | clear | 191 | 711 | none | 8.16 | none | 0.18 | 0 | 0
Upper Galleries | 2014-10-14 | URO5-3 |  | <0.009 | clear | 209 | 757 | none | 8.17 | none | 0.06 | 0 | 0
Zone 1 - North Front, Glacis Estate | 2014-10-20 | DO8-10 |  | <0.009 | clear | 190 | 712 | none | 8.27 | none | 0.1 | 0 | 0
Zone 2 - ICC | 2014-10-20 | DO8-11 |  | <0.009 | clear | 205 | 754 | none | 8.08 | none | 0.31 | 0 | 0
Zone3-ED- Highcliffe House | 2014-10-22 | DO8-12 |  | <0.009 | clear | 207 | 763 | none | 8.21 | none | 0.05 | 0 | 0
Moorish Castle tourist site | 2014-10-22 | URO5-4 |  | <0.009 | clear | 209 | 767 | none | 8.13 | none | 0.15 | 0 | 0
Zone 1 - Shipping, Gib Elec | 2014-10-29 | DO8-13 |  | <0.009 | clear | 211 | 757 | none | 8.27 | none | 0.2 | 0 | 0
Zone 2 - ICC | 2014-10-27 | DO8-14 |  | <0.009 | clear | 231 | 788 | none | 8.19 | none | 0.18 | 0 | 0
Zone3-ED- Clifftons | 2014-10-27 | DO8-15 |  | <0.009 | clear | 233 | 747 | none | 8.1 | none | 0.07 | 0 | 0
Devil's Gap | 2014-10-27 | URO5-5 |  | <0.009 | clear | 233 | 778 | none | 8.13 | none | 0.13 | 0 | 0
Zone1 - South District, Ragged Staff, AquaGib | 2014-11-03 | DN8-1 |  | <0.009 | clear | 212 | 749 | none | 8.07 | none | 0.24 | 0 | 0
Zone2-LL- Chronicle | 2014-11-03 | DN8-2 |  | <0.009 | clear | 222 | 735 | none | 7.93 | none | 0.17 | 0 | 0
Zone3-ED- Highcliffe House | 2014-11-03 | DN8-3 |  | <0.009 | clear | 216 | 782 | none | 8.01 | none | 0.12 | 0 | 0
Poca Rocca | 2014-11-05 | URN5-1 |  | <0.010 | clear | 225 | 795 | none | 8.23 | none | 0.1 | 0 | 0
Zone1 / Westisde,St Bernard's Hosp | 2014-11-10 | DN8-4 |  | <0.009 | clear | 214 | 769 | none | 8.26 | none | 0.07 | 0 | 0
Zone 2 - ICC | 2014-11-10 | DN8-5 |  | <0.009 | clear | 205 | 746 | none | 8.23 | none | -0.0033333 | 0 | 0
Zone 3 - Clifftons | 2014-11-12 | DN8-6 |  | <0.009 | clear | 216 | 785 | none | 8.21 | none | 0.05 | 0 | 0
Upper Galleries | 2014-11-12 | URN5-2 |  | <0.010 | clear | 214 | 773 | none | 8.21 | none | 0.11 | 0 | 0
Zone 1 - Moorish Castle, Keightley House | 2014-11-19 | DN8-7 |  | <0.009 | clear | 214 | 811 | none | 8.33 | none | 0.19 | 0 | 0
Zone 2 - John Mackintosh Hall | 2014-11-17 | DN8-8 |  | <0.009 | clear | 216 | 781 | none | 8.32 | none | 0.28 | 0 | 0
Zone 3 - Highcliffe House | 2014-11-17 | DN8-9 |  | <0.009 | clear | 218 | 810 | none | 8.29 | none | 0.06 | 0 | 0
Moorish Castle, tourist site | 2014-11-19 | URN5-3 |  | <0.010 | clear | 217 | 774 | none | 8.14 | none | 0.11 | 0 | 0
Zone 1 - High level, 10 Road to the Lines | 2014-11-26 | DN8-10 |  | <0.009 | clear | 207 | 725 | none | 8.28 | none | 0.34 | 0 | 0
Zone 2 - Kings Bastion Leisure | 2014-11-24 | DN8-11 |  | <0.009 | clear | 208 | 766 | none | 8.18 | none | 0.19 | 0 | 0
Zone 3 - Clifton Mews | 2014-11-24 | DN8-12 |  | <0.009 | clear | 193 | 697 | none | 8.25 | none | 0.08 | 0 | 0
Devil's Gap | 2014-11-26 | URN5-4 |  | <0.010 | clear | 200 | 725 | none | 8.29 | none | 0.1 | 0 | 0
Zone1 - South District, St Bernard's Road | 2014-12-03 | DD8-1 |  | <0.009 | clear | 208 | 742 | none | 8.26 | none | 0.11 | 0 | 0
Zone2-LL- Gavinos Passage | 2014-12-01 | DD8-2 |  | <0.009 | clear | 202 | 733 | none | 8.2 | none | 0.36 | 0 | 0
Zone3-ED- Highcliffe House | 2014-12-03 | DD8-3 |  | <0.009 | clear | 216 | 762 | none | 8.18 | none | 0.14 | 0 | 0
Poca Rocca | 2014-12-03 | URD5-1 |  | <0.009 | clear | 207 | 748 | none | 8.19 | none | 0.09 | 0 | 0
Zone 1 - North Front, Cemetry Office | 2014-12-10 | DD8-4 |  | <0.009 | clear | 198 | 690 | none | 8.02 | none | 0.13 | 0 | 0
Zone 2 - Casemates | 2014-12-10 | DD8-5 |  | <0.009 | clear | 196 | 724 | none | 8.12 | none | 0.18 | 0 | 0
Zone 3 - The Cliftons | 2014-12-08 | DD8-6 |  | <0.009 | clear | 181 | 645 | none | 7.94 | none | 0.09 | 0 | 0
Upper Galleries | 2014-12-10 | URD5-2 |  | <0.009 | clear | 193 | 676 | none | 8.17 | none | 0.09 | 0 | 0
Zone 1 - Shipping, Distiller | 2014-12-17 | DD8-7 |  | <0.009 | clear | 202 | 737 | none | 8.34 | none | 0.16 | 0 | 0
Zone 2 - Chronicle | 2014-12-17 | DD8-8 |  | <0.009 | clear | 214 | 728 | none | 8.15 | none | 0.18 | 0 | 0
Zone3-ED- Highcliffe House | 2014-12-17 | DD8-9 |  | <0.009 | clear | 208 | 768 | none | 8.26 | none | 0.07 | 0 | 0
Moorish castle tourist site | 2014-12-17 | URD5-3 |  | <0.009 | clear | 193 | 687 | none | 8.28 | none | 0.09 | 0 | 0
Zone 1 - Westside, Morrisons | 2014-12-22 | DD8-10 |  | <0.009 | clear | 204 | 712 | none | 7.96 | none | 0.13 | 0 | 0
Zone 2 - Piazza | 2014-12-22 | DD8-11 |  | <0.009 | clear | 199 | 728 | none | 8.01 | none | 0.27 | 0 | 0
Zone 3 - The Cliftons | 2014-12-22 | DD8-12 |  | <0.009 | clear | 195 | 683 | none | 8.06 | none | 0.07 | 0 | 0
Devil's Gap | 2014-12-22 | URD5-4 |  | <0.009 | clear | 197 | 692 | none | 8.02 | none | 0.16 | 0 | 0
Zone1 - Moorish Castle | 2015-01-07 | DJ25-1 |  | <0.009 | clear | 198 | 717 | none | 8.16 | none | 0.16 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2015-01-05 | DJ25-2 |  | <0.009 | clear | 200 | 724 | none | 8.15 | none | 0.2 | 0 | 0
Zone3-ED- Highcliffe House | 2015-01-05 | DJ25-3 |  | <0.009 | clear | 200 | 729 | none | 8.11 | none | 0.15 | 0 | 0
Zone 1 - Westside, Harbour Views | 2015-01-12 | DJ25-4 |  | <0.009 | clear | 194 | 710 | none | 8.38 | none | 0.06 | 0 | 0
Zone 2 - Kings Bastion Leisure Centre | 2015-01-12 | DJ25-5 |  | <0.009 | clear | 198 | 739 | none | 8.23 | none | 0.23 | 0 | 0
Zone 3 - Eliotts Battery | 2015-01-12 | DJ25-6 |  | <0.009 | clear | 192 | 702 | none | 8.25 | none | 0.07 | 0 | 0
Zone 1 - North Front, Tercentenary Stadium | 2015-01-26 | DJ25-7 |  | <0.009 | clear | 195 | 692 | none | 8.16 | none | 0.06 | 0 | 0
Zone 2 - Casemates | 2015-01-26 | DJ25-8 |  | <0.009 | clear | 203 | 730 | none | 7.95 | none | 0.23 | 0 | 0
Zone 3 - The Cliftons | 2015-01-26 | DJ25-9 |  | <0.009 | clear | 209 | 738 | none | 7.86 | none | 0.1 | 0 | 0
Zone1 - Shipping, AquaGib, M&E Dpt | 2015-02-03 | DF9-1 |  | <0.009 | clear | 198 | 721 | none | 7.92 | none | 0.17 | 0 | 0
Zone2-LL- ICC | 2015-02-03 | DF9-2 |  | <0.009 | clear | 201 | 730 | none | 7.95 | none | 0.17 | 0 | 0
Zone3-ED- Highcliffe House | 2015-02-03 | DF9-3 |  | <0.009 | clear | 195 | 710 | none | 8.08 | none | 0.09 | 0 | 0
Zone 1 - Westside, St Bernard's Hospital | 2015-02-09 | DF9-4 |  | <0.009 | clear | 200 | 760 | none | 8.02 | none | 0.08 | 0 | 0
Zone 2 - The Chronicle | 2015-02-09 | DF9-5 |  | <0.009 | clear | 195 | 727 | none | 8 | none | 0.26 | 0 | 0
Zone 3 - Clifton Mews | 2015-02-09 | DF9-6 |  | <0.009 | clear | 194 | 707 | none | 8.06 | none | 0.14 | 0 | 0
Zone 1 - High Level, Leanse Place | 2015-02-16 | DF9-7 |  | <0.009 | clear | 205 | 758 | none | 8.28 | none | 0.09 | 0 | 0
Zone 2 - Piazza | 2015-02-16 | DF9-8 |  | <0.009 | clear | 209 | 743 | none | 8.18 | none | 0.17 | 0 | 0
Zone 3 - Eliotts Battery | 2015-02-16 | DF9-9 |  | <0.009 | clear | 203 | 772 | none | 8.34 | none | 0.09 | 0 | 0
Zone 1 - Moorish Castle Estate | 2015-02-22 | DF9-10 |  | <0.009 | clear | 188 | 708 | none | 8.31 | none | 0.31 | 0 | 0
Zone 2 - Gib Oil | 2015-02-22 | DF9-11 |  | <0.009 | clear | 197 | 726 | none | 8.24 | none | 0.21 | 0 | 0
Zone3-ED- Highcliffe House | 2015-02-22 | DF9-12 |  | <0.009 | clear | 182 | 669 | none | 8.32 | none | 0.13 | 0 | 0
Zone 1 - North Front, Victoria Stadium | 2015-03-10 | DM17-1 |  | <0.009 | clear | 193 | 745 | none | 8.25 | none | 0.09 | 0 | 0
Zone 2 - Kings Bastion Leisure Centre | 2015-03-10 | DM17-2 |  | <0.009 | clear | 194 | 750 | none | 8.32 | none | 0.23 | 0 | 0
Zone 3 - Highcliffe House | 2015-03-10 | DM17-3 |  | <0.009 | clear | 192 | 738 | none | 8.28 | none | 0.38 | 0 | 0
Zone 1 - South Dist, Ragged Staff, AquaGib | 2015-03-17 | DM17-4 |  | <0.009 | clear | 178 | 774 | none | 8.23 | none | 0.11 | 0 | 0
Zone 2 - John Mackintosh Hall | 2015-03-17 | DM17-5 |  | <0.009 | clear | 203 | 770 | none | 8.17 | none | 0.14 | 0 | 0
Zone 3 - Eliotts Battery | 2015-03-17 | DM17-6 |  | <0.009 | clear | 208 | 780 | none | 8.2 | none | 0.07 | 0 | 0
Zone 1 - Shipping, AquaGib, Distiller | 2015-03-23 | DM17-7 |  | <0.009 | clear | 195 | 701 | none | 8.23 | none | 0.19 | 0 | 0
Zone 2 - Casemates | 2015-03-23 | DM17-8 |  | <0.009 | clear | 198 | 677 | none | 8.27 | none | 0.23 | 0 | 0
Zone 3 - Highcliffe House | 2015-03-23 | DM17-9 |  | <0.009 | clear | 156 | 565 | none | 8.21 | none | 0.1 | 0 | 0
Zone1 - High Level, Tank Ramp | 2015-04-22 | DA17-1 |  | <0.009 | clear | 204 | 765 | none | 8.07 | none | 0.12 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2015-04-22 | DA17-2 |  | <0.009 | clear | 198 | 764 | none | 8.11 | none | 0.12 | 0 | 0
Zone3-ED- Clifton Mews | 2015-04-22 | DA17-3 |  | <0.009 | clear | 198 | 767 | none | 8.08 | none | 0.15 | 0 | 0
Zone1-Moorish Castle Estate, Key Way Hse | 2015-04-28 | DA17-4 |  | <0.009 | clear | 210 | 791 | none | 8.11 | none | 0.09 | 0 | 0
Zone 2 - The Chronical, Casemates | 2015-04-28 | DA17-5 |  | <0.009 | clear | 205 | 781 | none | 8.06 | none | 0.12 | 0 | 0
Zone 3 - Eliotts Battery | 2015-04-28 | DA17-6 |  | <0.009 | clear | 212 | 795 | none | 7.99 | none | 0.09 | 0 | 0
Zone1 - North Front, Cementry Office | 2015-05-04 | DM18-1 |  | <0.009 | clear | 195 | 768 | none | 7.98 | none | 0.09 | 0 | 0
Zone2-LL- Piazza | 2015-05-04 | DM18-2 |  | <0.009 | clear | 205 | 781 | none | 8.06 | none | 0.11 | 0 | 0
Zone 3 - Cliffton Mews | 2015-05-04 | DM18-3 |  | <0.009 | clear | 198 | 764 | none | 8.12 | none | 0.09 | 0 | 0
Zone1 - South District, Ragged Staff | 2015-05-10 | DM18-4 |  | <0.009 | clear | 203 | 784 | none | 7.9 | none | 0.16 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2015-05-11 | DM18-5 |  | <0.009 | clear | 197 | 740 | none | 7.97 | none | 0.09 | 0 | 0
Zone 3 - Highcliffe House | 2015-05-10 | DM18-6 |  | <0.009 | clear | 198 | 745 | none | 7.99 | none | 0.08 | 0 | 0
Zone1 - Shipping, AquaGib, Distiller kitchen | 2015-05-18 | DM18-7 |  | <0.009 | clear | 214 | 794 | none | 8.08 | none | 0.1 | 0 | 0
Zone2-LL- New Passage | 2015-05-18 | DM18-8 |  | <0.009 | clear | 204 | 777 | none | 8.12 | none | 0.16 | 0 | 0
Zone 3 - Eliotts Battery | 2015-05-18 | DM18-9 |  | <0.009 | clear | 208 | 778 | none | 8.17 | none | 0.11 | 0 | 0
Zone1 - Westside, St Bernard's Hospital | 2015-05-26 | DM18-10 |  | <0.009 | clear | 197 | 769 | none | 7.8 | none | 0.14 | 0 | 0
Zone2-LL- Casemates | 2015-05-26 | DM18-11 |  | <0.009 | clear | 198 | 787 | none | 7.85 | none | 0.38 | 0 | 0
Zone 3 - Cliffton Mews | 2015-05-26 | DM18-12 |  | <0.009 | clear | 157 | 634 | none | 7.97 | none | 0.12 | 0 | 0
Zone1 - North Front, Cementry Office | 2015-06-01 | DJ26-1 |  | <0.009 | clear | 199 | 793 | none | 8.01 | none | 0.1 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2015-06-01 | DJ26-2 |  | <0.009 | clear | 215 | 817 | none | 8.02 | none | 0.12 | 0 | 0
Zone 3 - Sunset Close | 2015-06-01 | DJ26-3 |  | <0.009 | clear | 222 | 843 | none | 8.24 | none | 0.09 | 0 | 0
Zone1 - Moorish Castle | 2015-06-10 | DJ26-4 |  | <0.009 | clear | 218 | 866 | none | 8.13 | none | 0.16 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2015-06-08 | DJ26-5 |  | <0.009 | clear | 206 | 807 | none | 8.04 | none | 0.59 | 0 | 0
Zone 3 - Cliffton Mews | 2015-06-08 | DJ26-6 |  | <0.009 | clear | 220 | 865 | none | 8.09 | none | 0.09 | 0 | 0
Zone1 - North Front, Tercentenary Sports Hall | 2015-06-16 | DJ26-7 |  | <0.009 | clear | 219 | 814 | none | 8.18 | none | 0.07 | 0 | 0
Zone2-LL- Piazza | 2015-06-16 | DJ26-8 |  | <0.009 | clear | 204 | 819 | none | 8.08 | none | 0.11 | 0 | 0
Zone 3 - Cliffton Mews | 2015-06-16 | DJ26-9 |  | <0.009 | clear | 195 | 783 | none | 8.15 | none | 0.09 | 0 | 0
Zone1 - South District, Veterinary Clinic | 2015-06-24 | DJ26-10 |  | <0.009 | clear | 208 | 804 | none | 8.09 | none | 0.15 | 0 | 0
Zone2-LL- Kings Bastion, Leisure Centre | 2015-06-22 | DJ26-11 |  | <0.009 | clear | 217 | 809 | none | 8.3 | none | 0.29 | 0 | 0
Zone 3 - Eliotts Battery | 2015-06-22 | DJ26-12 |  | <0.009 | clear | 226 | 822 | none | 8.17 | none | 0.08 | 0 | 0
Zone1 - Shipping, AquagGib, M&E dept | 2015-06-30 | DJ27-1 |  | <0.009 | clear | 229 | 820 | none | 8.07 | none | 0.18 | 0 | 0
Zone2-LL- Casemates | 2015-06-30 | DJ27-2 |  | <0.009 | clear | 200 | 808 | none | 8.14 | none | 0.24 | 0 | 0
Zone 3 - Highcliffe | 2015-06-30 | DJ27-3 |  | <0.009 | clear | 227 | 847 | none | 8.21 | none | 0.1 | 0 | 0
Zone1 - Westside, Post Depot | 2015-07-08 | DJ27-4 |  | <0.009 | clear | 212 | 826 | none | 7.95 | none | 0.1 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2015-07-08 | DJ27-5 |  | <0.009 | clear | 207 | 761 | none | 7.98 | none | 0.13 | 0 | 0
Zone 3 - Cliffton Mews | 2015-07-08 | DJ27-6 |  | <0.009 | clear | 211 | 814 | none | 8.07 | none | 0.08 | 0 | 0
Zone1 - HL, Leanse Place, AquaGib office | 2015-07-15 | DJ27-7 |  | <0.009 | clear | 209 | 824 | none | 8.04 | none | 0.08 | 0 | 0
Zone2-LL- The Chronicle | 2015-07-13 | DJ27-8 |  | <0.009 | clear | 210 | 812 | none | 7.98 | none | 2.23 | 0 | 0
Zone 3 - Sunset Close | 2015-07-13 | DJ27-9 |  | <0.009 | clear | 199 | 799 | none | 8.08 | none | 0.15 | 0 | 0
Zone1 - North Front, Both Worlds | 2015-07-23 | DJ27-10 |  | <0.009 | clear | 200 | 790 | none | 8.05 | none | 0.14 | 0 | 0
Zone2-LL- Piazza | 2015-07-20 | DJ27-11 |  | <0.009 | clear | 214 | 821 | none | 8.05 | none | 0.67 | 0 | 0
Zone 3 - Eliotts Battery | 2015-07-23 | DJ27-12 |  | <0.009 | clear | 202 | 737 | none | 8.1 | none | 0.19 | 0 | 0
Zone 1 - South District, 4 Stagioni | 2015-07-28 | DJ27-13 |  | <0.009 | clear | 221 | 848 | none | 7.82 | none | 0.25 | 0 | 0
Zone 2 - Lesuire Centre | 2015-07-27 | DJ27-14 |  | <0.009 | clear | 212 | 818 | none | 8.2 | none | 0.23 | 0 | 0
Zone 3 - The Clifftons | 2015-07-28 | DJ27-15 |  | <0.009 | clear | 240 | 923 | none | 8.15 | none | 0.21 | 0 | 0
Zone1 - Shipping, AquagGib, Distiller | 2015-08-03 | DA18-1 |  | <0.009 | clear | 193 | 818 | none | 8.16 | none | 0.26 | 0 | 0
Zone2-LL- Casemates | 2015-08-03 | DA18-2 |  | <0.009 | clear | 197 | 833 | none | 8.04 | none | 0.65 | 0 | 0
Zone 3 - Highcliffe House | 2015-08-03 | DA18-3 |  | <0.009 | clear | 212 | 801 | none | 8.19 | none | 0.16 | 0 | 0
Zone1 - Harbour Views | 2015-08-12 | DA18-4 |  | <0.009 | clear | 234 | 889 | none | 8.17 | none | 0.13 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2015-08-12 | DA18-5 |  | <0.009 | clear | 231 | 854 | none | 8.17 | none | 0.12 | 0 | 0
Zone 3 - The Clifftons | 2015-08-12 | DA18-6 |  | <0.009 | clear | 232 | 884 | none | 8.27 | none | 0.13 | 0 | 0
Zone1 - Moorish Castle Estate | 2015-08-17 | DA18-7 |  | <0.009 | clear | 215 | 830 | none | 8.33 | none | 0.18 | 0 | 0
Zone 2 - The Chronicle | 2015-08-17 | DA18-8 |  | <0.009 | clear | 216 | 800 | none | 8.17 | none | 0.48 | 0 | 0
Zone 3 - Eliotts Battery | 2015-08-17 | DA18-9 |  | <0.009 | clear | 215 | 820 | none | 8.21 | none | 0.26 | 0 | 0
Zone1 - North Front Cementry Office | 2015-08-25 | DA18-10 |  | <0.009 | clear | 220 | 831 | none | 8.12 | none | 0.12 | 0 | 0
Zone2-LL- Kings Bastion Lesuire Centre | 2015-08-25 | DA18-11 |  | <0.009 | clear | 220 | 837 | none | 8.25 | none | 0.19 | 0 | 0
Zone 3 - Clifftons | 2015-08-25 | DA18-12 |  | <0.009 | clear | 229 | 850 | none | 8.2 | none | 0.1 | 0 | 0
Zone1 - South District, Alameda Estate | 2015-09-01 | DS9-1 |  | <0.009 | clear | 214 | 837 | none | 8.24 | none | 0.16 | 0 | 0
Zone2-LL- Kings Bastion Lesuire Centre | 2015-09-01 | DS9-2 |  | <0.009 | clear | 216 | 838 | none | 8.21 | none | 0.38 | 0 | 0
Zone 3 - Highcliffe House | 2015-09-01 | DS9-3 |  | <0.009 | clear | 205 | 811 | none | 8.26 | none | 0.25 | 0 | 0
Zone1 - Shipping, Gib Elec security post | 2015-09-08 | DS9-4 |  | <0.009 | clear | 208 | 825 | none | 8.13 | none | 0.31 | 0 | 0
Zone2-LL- Casemates | 2015-09-08 | DS9-5 |  | <0.009 | clear | 207 | 847 | none | 8.06 | none | 0.29 | 0 | 0
Zone 3 - Eliotts Battery | 2015-09-08 | DS9-6 |  | <0.009 | clear | 212 | 852 | none | 8.04 | none | 0.15 | 0 | 0
Zone1 - Westside, Varyl Begg Estate | 2015-09-14 | DS9-7 |  | <0.009 | clear | 202 | 793 | none | 8.16 | none | 0.31 | 0 | 0
Zone 2 - John Mackintosh Hall | 2015-09-14 | DS9-8 |  | <0.009 | clear | 195 | 788 | none | 8.13 | none | 0.25 | 0 | 0
Zone 3 - Clifftons | 2015-09-14 | DS9-9 |  | <0.009 | clear | 199 | 775 | none | 8.17 | none | 0.26 | 0 | 0
Zone1 - High Level, Tank Ramp | 2015-09-23 | DS9-10 |  | <0.009 | clear | 215 | 847 | none | 8.13 | none | 0.22 | 0 | 0
Zone2-LL- Piazza | 2015-09-21 | DS9-11 |  | <0.009 | clear | 210 | 818 | none | 8.09 | none | 1.92 | 0 | 0
Zone 3 - Cliffton Mews | 2015-09-23 | DS9-12 |  | <0.009 | clear | 203 | 807 | none | 8.11 | none | 0.25 | 0 | 0
Zone 1 - Moorish Castle Estate | 2015-09-28 | DS9-13 |  | <0.009 | clear | 203 | 789 | none | 8.16 | none | 0.22 | 0 | 0
Zone2-LL- Kings Bastion Lesuire Centre | 2015-09-28 | DS9-14 |  | <0.009 | clear | 214 | 822 | none | 8.14 | none | 0.31 | 0 | 0
Zone 3 - Eliotts Battery | 2015-09-28 | DS9-15 |  | <0.009 | clear | 198 | 796 | none | 8.07 | none | 0.32 | 0 | 0
Zone1 - North Front, Cementry Road | 2015-10-05 | DO9-1 |  | <0.009 | clear | 206 | 816 | none | 8.17 | none | 0.62 | 0 | 0
Zone2-LL-Watergate House,Casemates Sq | 2015-10-05 | DO9-2 |  | <0.009 | clear | 205 | 828 | none | 8.1 | none | 0.13 | 0 | 0
Zone 3 - Highcliffe House | 2015-10-05 | DO9-3 |  | <0.009 | clear | 203 | 832 | none | 8.14 | none | 0.15 | 0 | 0
Zone1 - SD, AquaGib, Ragged Staff depot | 2015-10-13 | DO9-4 |  | <0.009 | clear | 175 | 703 | none | 8.17 | none | 0.38 | 0 | 0
Zone2-LL- Casemates | 2015-10-13 | DO9-5 |  | <0.009 | clear | 195 | 784 | none | 8.16 | none | 0.83 | 0 | 0
Zone 3 - The Cliftons | 2015-10-13 | DO9-6 |  | <0.009 | clear | 193 | 753 | none | 8.17 | none | 0.25 | 0 | 0
Zone1 - Shipping, AquaGib Waterport depot | 2015-10-21 | DO9-7 |  | <0.009 | clear | 195 | 763 | none | 8.08 | none | 0.19 | 0 | 0
Zone 2 - John Mackintosh Hall | 2015-10-21 | DO9-8 |  | <0.009 | clear | 206 | 781 | none | 8.08 | none | 0.27 | 0 | 0
Zone 3 - Eliotts Battery | 2015-10-21 | DO9-9 |  | <0.009 | clear | 204 | 808 | none | 8.12 | none | 0.15 | 0 | 0
Zone1 - Westside, St Bernard's Hospital | 2015-10-28 | DO9-10 |  | <0.009 | clear | 206 | 844 | none | 7.99 | none | 0.25 | 0 | 0
Zone2-LL- ICC | 2015-10-28 | DO9-11 |  | <0.009 | clear | 214 | 805 | none | 8.12 | none | 0.41 | 0 | 0
Zone 3 - Highcliffe House | 2015-10-28 | DO9-12 |  | <0.009 | clear | 197 | 777 | none | 8.03 | none | 0.31 | 0 | 0
Zone1 - High Level, Leanse Place | 2015-11-05 | DN9-1 |  | <0.009 | clear | 203 | 791 | none | 8.08 | none | 0.17 | 0 | 0
Zone2-LL- O'Callaghan, Eliotts Hotel | 2015-11-03 | DN9-2 |  | <0.009 | clear | 205 | 788 | none | 8.06 | none | 0.57 | 0 | 0
Zone 3 - Clifton Mews | 2015-11-05 | DN9-3 |  | <0.009 | clear | 192 | 750 | none | 8.14 | none | 0.19 | 0 | 0
Zone1 - Moorish Castle Estate | 2015-11-11 | DN9-4 |  | <0.009 | clear | 192 | 759 | none | 8.11 | none | 0.18 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2015-11-11 | DN9-5 |  | <0.009 | clear | 205 | 802 | none | 8.1 | none | 0.21 | 0 | 0
Zone 3 - Eliotts Battery | 2015-11-11 | DN9-6 |  | <0.009 | clear | 191 | 744 | none | 8.11 | none | 0.2 | 0 | 0
Zone1 - North Front, Cementry Office | 2015-11-18 | DN9-7 |  | <0.009 | clear | 205 | 785 | none | 8.22 | none | 0.29 | 0 | 0
Zone 2 - LL Casemates Square | 2015-11-18 | DN9-8 |  | <0.009 | clear | 203 | 786 | none | 8.17 | none | 0.43 | 0 | 0
Zone 3 - Cliffton Mews | 2015-11-18 | DN9-9 |  | <0.009 | clear | 208 | 814 | none | 8.2 | none | 0.2 | 0 | 0
Zone1 - Shipping, Gib Elec | 2015-12-02 | DD9-1 |  | <0.009 | clear | 207 | 802 | none | 8.29 | none | 0.16 | 0 | 0
Zone2-LL- Piazza | 2015-12-02 | DD9-2 |  | <0.009 | clear | 203 | 783 | none | 8.21 | none | 0.34 | 0 | 0
Zone3-ED- Eliotts Battery | 2015-12-02 | DD9-3 |  | <0.009 | clear | 197 | 780 | none | 8.16 | none | 0.17 | 0 | 0
Zone 1 - Westside, St Bernard's Hospital | 2015-12-09 | DD9-4 |  | <0.009 | clear | 212 | 833 | none | 8.08 | none | 0.17 | 0 | 0
Zone 2 - ICC | 2015-12-09 | DD9-5 |  | <0.009 | clear | 205 | 790 | none | 8.14 | none | 0.21 | 0 | 0
Zone 3 - Cliffton Mews | 2015-12-09 | DD9-6 |  | <0.009 | clear | 203 | 803 | none | 8.22 | none | 0.19 | 0 | 0
Zone 1 - High Level, Arengo's nursery | 2015-12-17 | DD9-7 |  | <0.009 | clear | 205 | 796 | none | 7.93 | none | 0.3 | 0 | 0
Zone 2 - Kings Bastion Leisure Centre | 2015-12-17 | DD9-8 |  | <0.009 | clear | 200 | 790 | none | 7.96 | none | 0.21 | 0 | 0
Zone 3 - Highcliffe | 2015-12-17 | DD9-9 |  | <0.009 | clear | 211 | 823 | none | 7.95 | none | 0.2 | 0 | 0
Zone 1 - NF,Cemetry Road, The Corner Shop | 2015-12-21 | DD9-10 |  | <0.009 | clear | 204 | 783 | none | 8.18 | none | 0.28 | 0 | 0
Zone 2 - Gib Oil, Line Wall Road | 2015-12-21 | DD9-11 |  | <0.009 | clear | 217 | 787 | none | 8.22 | none | 0.31 | 0 | 0
Zone 3 - Cliffton Mews | 2015-12-21 | DD9-12 |  | <0.009 | clear | 212 | 837 | none | 8.17 | none | 0.26 | 0 | 0
Zone 1 - Moorish Castle Estate | 2015-12-29 | DD9-13 |  | <0.009 | clear | 178 | 701 | none | 8.24 | none | 0.17 | 0 | 0
Zone 2 - Casemates | 2015-12-29 | DD9-14 |  | <0.009 | clear | 194 | 762 | none | 8.22 | none | 0.21 | 0 | 0
Zone 3 - Eliotts Battery | 2015-12-29 | DD9-15 |  | 0.017 | clear | 177 | 694 | none | 8.18 | none | 0.24 | 0 | 0
Zone1 - South District, New Harbours, Gibtel | 2016-01-06 | DJ28-1 |  | <0.009 | clear | 190 | 737 | none | 8.16 | none | 0.25 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2016-01-06 | DJ28-2 |  | <0.009 | clear | 189 | 747 | none | 8.09 | none | 0.13 | 0 | 0
Zone3-ED- Highcliffe House | 2016-01-04 | DJ28-3 |  | 0.011 | clear | 198 | 767 | none | 8.05 | none | 0.19 | 0 | 0
Zone 4-Upper rock,Moorish Castle tourist site | 2016-01-06 | DJ28-4 |  | <0.009 | clear | 180 | 691 | none | 8.19 | none | 0.19 | 0 | 0
Zone1 - Shipping, Distiller, AquaGib | 2016-01-11 | DJ28-5 |  | <0.009 | clear | 193 | 757 | none | 8.3 | none | 0.15 | 0 | 0
Zone2-LL- Piazza | 2016-01-13 | DJ28-6 |  | <0.009 | clear | 199 | 759 | none | 7.95 | none | 0.29 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-01-13 | DJ28-7 |  | <0.009 | clear | 199 | 697 | none | 8.06 | none | 0.28 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2016-01-11 | DJ28-8 |  | 0.01 | clear | 188 | 734 | none | 8.2 | none | 0.2 | 0 | 0
Zone1 - Westside, Waterport | 2016-01-21 | DJ28-9 |  | <0.009 | clear | 202 | 794 | none | 8.29 | none | 0.24 | 0 | 0
Zone2-LL- ICC | 2016-01-21 | DJ28-10 |  | <0.009 | clear | 195 | 783 | none | 8.24 | none | 0.26 | 0 | 0
Zone3-ED- Highcliffe House | 2016-01-21 | DJ28-11 |  | 0.009 | clear | 205 | 795 | none | 8.22 | none | 0.22 | 0 | 0
Zone 4 - Upper rock, Lower Bruces Farm | 2016-01-21 | DJ28-12 |  | <0.009 | clear | 185 | 683 | none | 7.99 | none | 0.23 | 0 | 0
Zone1 - Shipping, Distiller kitchen, AquaGib | 2016-01-25 | DJ28-13 |  | <0.009 | clear | 203 | 748 | none | 7.93 | none | 0.22 | 0 | 0
Zone2-LL- ICC | 2016-01-27 | DJ28-14 |  | <0.009 | clear | 197 | 771 | none | 7.92 | none | 0.29 | 0 | 0
Zone3-ED- Buena Vista Estate | 2016-01-25 | DJ28-15 |  | 1.009 | clear | 206 | 756 | none | 8.04 | none | 0.18 | 0 | 0
Zone 4 - Upper rock, Upper Galleries | 2016-01-27 | DJ28-16 |  | <0.010 | clear | 192 | 766 | none | 8.14 | none | 0.21 | 0 | 0
Zone1 - South District, New Harbours, Gibtel | 2016-02-03 | DF10-1 |  | <0.009 | clear | 203 | 776 | none | 8.49 | none | 0.24 | 0 | 0
Zone2-LL- Duke of Kent House | 2016-02-01 | DF10-2 |  | <0.009 | clear | 203 | 735 | none | 8.38 | none | 0.4 | 0 | 0
Zone3-ED- Highcliffe House | 2016-02-03 | DF10-3 |  | <0.009 | clear | 201 | 777 | none | 8.35 | none | 0.17 | 0 | 0
Zone 4-Upper rock, Moorish Castle tourist site | 2016-02-01 | DF10-4 |  | <0.009 | clear | 198 | 760 | none | 8.4 | none | 0.32 | 0 | 0
Zone1 - North Front, Glacis Estate | 2016-02-11 | DF10-5 |  | <0.009 | clear | 195 | 774 | none | 8.08 | none | 0.12 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2016-02-11 | DF10-6 |  | <0.009 | clear | 193 | 757 | none | 8.09 | none | 0.22 | 0 | 0
Zone3-ED- Highcliffe House | 2016-02-11 | DF10-7 |  | <0.009 | clear | 195 | 775 | none | 8.16 | none | 0.19 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2016-02-08 | DF10-8 |  | <0.009 | clear | 192 | 761 | none | 8.21 | none | 0.16 | 0 | 0
Zone1- Moorish Castle Estate, Oli's Takeaway | 2016-02-15 | DF10-9 |  | <0.009 | clear | 198 | 764 | none | 7.71 | none | 0.3 | 0 | 0
Zone2-LL- ICC | 2016-02-15 | DF10-10 |  | <0.009 | clear | 203 | 791 | none | 8.18 | none | 0.24 | 0 | 0
Zone3-ED- Clifton Mews | 2016-02-15 | DF10-11 |  | <0.009 | clear | 195 | 760 | none | 8.12 | none | 0.29 | 0 | 0
Zone 4 - Upper rock, Lower Bruces Farm | 2016-02-15 | DF10-12 |  | <0.009 | clear | 202 | 759 | none | 8.15 | none | 0.13 | 0 | 0
Zone1-SDistrict, AquaGib, Ragged Staff depot | 2016-02-25 | DF10-13 |  | <0.009 | clear | 195 | 732 | none | 8.27 | none | 0.23 | 0 | 0
Zone2-LL- Chronicle | 2016-02-25 | DF10-14 |  | <0.009 | clear | 197 | 796 | none | 8.18 | none | 0.12 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-02-25 | DF10-15 |  | <0.009 | clear | 207 | 765 | none | 8.11 | none | 0.21 | 0 | 0
Zone 4 - Upper Galleries | 2016-02-25 | DF10-16 |  | <0.009 | clear | 215 | 791 | none | 8.17 | none | 0.18 | 0 | 0
Zone1 - Shipping, Gib Elec | 2016-02-29 | DM19-1 |  | <0.009 | clear | 189 | 675 | none | 8.3 | none | 0.29 | 0 | 0
Zone2-LL- Casemates | 2016-02-29 | DM19-2 |  | <0.009 | clear | 194 | 702 | none | 8.2 | none | 0.21 | 0 | 0
Zone3-ED- Highcliffe House | 2016-03-02 | DM19-3 |  | <0.009 | clear | 205 | 786 | none | 8.16 | none | 0.25 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2016-03-02 | DM19-4 |  | <0.009 | clear | 207 | 763 | none | 8.19 | none | 0.22 | 0 | 0
Zone1 - High Level, Leanse Place | 2016-03-07 | DM19-5 |  | <0.009 | clear | 198 | 747 | none | 8.16 | none | 0.14 | 0 | 0
Zone2-LL- Piazza | 2016-03-09 | DM19-6 |  | <0.009 | clear | 197 | 772 | none | 8.05 | none | 0.28 | 0 | 0
Zone3-ED- Clifton Mews | 2016-03-09 | DM19-7 |  | <0.009 | clear | 212 | 810 | none | 8.02 | none | 0.14 | 0 | 0
Zone 4 - Moorish Castle, tourist site | 2016-03-09 | DM19-8 |  | <0.009 | clear | 201 | 761 | none | 8.04 | none | 0.22 | 0 | 0
Zone1 - North Front, Cemetry office | 2016-03-15 | DM19-9 |  | <0.009 | clear | 186 | 742 | none | 8.05 | none | 0.22 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2016-03-15 | DM19-10 |  | <0.009 | clear | 198 | 790 | none | 8.13 | none | 0.14 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-03-15 | DM19-11 |  | <0.009 | clear | 197 | 774 | none | 8.11 | none | 0.2 | 0 | 0
Zone 4- U.R,Lower Bruces Farm sampling tap | 2016-03-15 | DM19-12 |  | <0.009 | clear | 198 | 786 | none | 8.07 | none | 0.24 | 0 | 0
Zone1 - Moorish Castle Estate, Key House | 2016-03-22 | DM19-13 |  | <0.009 | clear | 184 | 722 | none | 8.18 | none | 0.13 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2016-03-22 | DM19-14 |  | <0.009 | clear | 198 | 755 | none | 8.11 | none | 0.14 | 0 | 0
Zone3-ED- Highcliffe House | 2016-03-22 | DM19-15 |  | <0.009 | clear | 206 | 774 | none | 8.1 | none | 0.22 | 0 | 0
Zone 4 - Upper Galleries | 2016-03-22 | DM19-16 |  | <0.009 | clear | 201 | 764 | none | 8.14 | none | 0.14 | 0 | 0
Zone1 - South District, Ragged Staff | 2016-03-29 | DM19-17 |  | <0.009 | clear | x | 773 | none | 7.98 | none | 0.97 | 0 | 0
Zone2-LL- ICC | 2016-03-29 | DM19-18 |  | <0.009 | clear | x | 748 | none | 8.04 | none | 0.29 | 0 | 0
Zone3-ED- Clifton Mews | 2016-03-30 | DM19-19 |  | <0.009 | clear | x | 765 | none | 8.21 | none | 0.21 | 0 | 0
Zone 4 - Poca Rocca | 2016-03-29 | DM19-20 |  | <0.009 | clear | x | 780 | none | 8.08 | none | 0.15 | 0 | 0
Zone1 - Shipping, Distiller | 2016-04-06 | DA19-1 |  | <0.009 | clear | x | 744 | none | 8.25 | none | 0.28 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2016-04-06 | DA19-2 |  | <0.009 | clear | x | 750 | none | 8.18 | none | 0.14 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-04-06 | DA19-3 |  | <0.009 | clear | x | 750 | none | 8.22 | none | 0.23 | 0 | 0
Zone 4 - U,R, Moorish Castle, tourist site | 2016-04-06 | DA19-4 |  | <0.009 | clear | x | 774 | none | 8.19 | none | 0.18 | 0 | 0
Zone1 - High Level, Arengo's nursery | 2016-04-13 | DA19-5 |  | <0.009 | clear | x | 713 | none | 8.32 | none | 0.23 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2016-04-13 | DA19-6 |  | <0.009 | clear | x | 753 | none | 8.37 | none | 0.25 | 0 | 0
Zone3-ED- Highcliffe House | 2016-04-13 | DA19-7 |  | <0.009 | clear | x | 852 | none | 8.22 | none | 0.17 | 0 | 0
Zone 4- U.R,Lower Bruces Farm sampling tap | 2016-04-11 | DA19-8 |  | <0.009 | clear | x | 791 | none | 8.25 | none | 0.15 | 0 | 0
Zone1 - North Front, The Paint Shop | 2016-04-21 | DA19-9 |  | <0.009 | clear | x | 673 | none | 8.27 | none | 0.39 | 0 | 0
Zone2-LL- Piazza | 2016-04-21 | DA19-10 |  | <0.009 | clear | x | 789 | none | 8.17 | none | 0.26 | 0 | 0
Zone3-ED- Highcliffe House | 2016-04-21 | DA19-11 |  | <0.009 | clear | x | 755 | none | 8.29 | none | 0.25 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2016-04-21 | DA19-12 |  | <0.009 | clear | x | 791 | none | 8.19 | none | 0.18 | 0 | 0
Zone1 - Moorish Castle Estate | 2016-04-26 | DA19-13 |  | <0.009 | clear | x | 819 | none | 8.18 | none | 0.19 | 0 | 0
Zone2-LL- Cheers, Cornwalls Centre | 2016-04-25 | DA19-14 |  | <0.009 | clear | x | 793 | none | 8.1 | none | 0.32 | 0 | 0
Zone3-ED- Clifton Mews | 2016-04-26 | DA19-15 |  | <0.009 | clear | x | 826 | none | 8.14 | none | 0.25 | 0 | 0
Zone 4 - Poca Rocca | 2016-04-25 | DA19-16 |  | <0.009 | clear | x | 830 | none | 8.11 | none | 0.17 | 0 | 0
Zone1 - South District, Ragged Staff | 2016-05-04 | DM20-1 |  | <0.009 | clear | 235 | 749 | none | 8.14 | none | 0.31 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2016-05-04 | DM20-2 |  | <0.009 | clear | 181 | 781 | none | 8.1 | none | 0.24 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-05-04 | DM20-3 |  | <0.009 | clear | 320 | 785 | none | 7.99 | none | 0.19 | 0 | 0
Zone 4 - U,R, Moorish Castle, tourist site | 2016-05-04 | DM20-4 |  | <0.009 | clear | 229 | 813 | none | 8.05 | none | 0.17 | 0 | 0
Zone1 - Shipping, Gibraltar Pilots | 2016-05-11 | DM20-5 |  | <0.009 | clear | 198 | 771 | none | 8.22 | none | 0.26 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2016-05-11 | DM20-6 |  | <0.009 | clear | 196 | 779 | none | 8.2 | none | 0.2 | 0 | 0
Zone3-ED- Highcliffe House | 2016-05-11 | DM20-7 |  | <0.009 | clear | 212 | 917 | none | 8.18 | none | 0.26 | 0 | 0
Zone 4- U.R,Lower Bruces Farm sampling tap | 2016-05-11 | DM20-8 |  | <0.009 | clear | 241 | 863 | none | 8.22 | none | 0.21 | 0 | 0
Zone1 - North Front, The Paint Shop | 2016-05-18 | DM20-9 |  | <0.009 | clear | 213 | 787 | none | 8.23 | none | 0.19 | 0 | 0
Zone2-LL- Piazza | 2016-05-18 | DM20-10 |  | <0.009 | clear | 211 | 777 | none | 8.2 | none | 0.3 | 0 | 0
Zone3-ED- Highcliffe House | 2016-05-18 | DM20-11 |  | <0.009 | clear | 189 | 876 | none | 8.2 | none | 0.14 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2016-05-18 | DM20-12 |  | <0.009 | clear | 228 | 865 | none | 8.23 | none | 0.17 | 0 | 0
Zone1 - N.Front,Tercentenary Sports Complex | 2016-05-23 | DM20-13 |  | <0.009 | clear | 169 | 753 | none | 8.18 | none | 0.29 | 0 | 0
Zone2-LL- ICC | 2016-05-23 | DM20-14 |  | <0.009 | clear | 208 | 708 | none | 8.3 | none | 0.15 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-05-23 | DM20-15 |  | <0.009 | clear | 176 | 735 | none | 8.17 | none | 0.17 | 0 | 0
Zone 4 - Poca Rocca | 2016-05-24 | DM20-16 |  | <0.009 | clear | 235 | 764 | none | 8.16 | none | 0.13 | 0 | 0
Zone1 - South District, Ragged Staff | 2016-05-31 | DJ29-1 |  | <0.009 | clear | 201 | 813 | none | 8.11 | none | 0.15 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2016-05-31 | DJ29-2 |  | <0.009 | clear | 240 | 814 | none | 8.09 | none | 0.17 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-05-31 | DJ29-3 |  | <0.009 | clear | 229 | 781 | none | 8.05 | none | 0.29 | 0 | 0
Zone 4 - Upper Rock, M.Castle, tourist site | 2016-05-31 | DJ29-4 |  | <0.009 | clear | 231 | 825 | none | 8.03 | none | 0.14 | 0 | 0
Zone1 - MC Estate, Anderson Hse, Calpe Rd | 2016-06-09 | DJ29-5 |  | <0.009 | clear | 145 | 794 | none | 8.21 | none | 0.22 | 0 | 0
Zone2-LL- Casemates | 2016-06-06 | DJ29-6 |  | <0.009 | clear | 215 | 821 | none | 8.26 | none | 0.24 | 0 | 0
Zone3-ED- Highcliffe House | 2016-06-06 | DJ29-7 |  | <0.009 | clear | 218 | 875 | none | 8.28 | none | 0.12 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2016-06-09 | DJ29-8 |  | <0.009 | clear | 234 | 886 | none | 8.16 | none | 0.1 | 0 | 0
Zone1 - High Level, Leanse Place | 2016-06-15 | DJ29-9 |  | <0.009 | clear | 178 | 739 | none | 8.11 | none | 0.12 | 0 | 0
Zone2-LL- Piazza | 2016-06-15 | DJ29-10 |  | <0.009 | clear | 221 | 807 | none | 8.04 | none | 0.11 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-06-15 | DJ29-11 |  | <0.009 | clear | 236 | 812 | none | 7.99 | none | 0.12 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2016-06-15 | DJ29-12 |  | <0.009 | clear | 197 | 843 | none | 8.05 | none | 0.18 | 0 | 0
Zone1 - North Front, Paint Shop | 2016-06-22 | DJ29-13 |  | <0.009 | clear | 201 | 791 | none | 7.96 | none | 0.18 | 0 | 0
Zone2-LL- Line Wall Road, Gib Oil | 2016-06-22 | DJ29-14 |  | <0.009 | clear | 223 | 782 | none | 7.47 | none | 0.22 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-06-20 | DJ29-15 |  | <0.009 | clear | 218 | 794 | none | 8.27 | none | 0.15 | 0 | 0
Zone 4 - U R, Upper Galleries, lower toilets | 2016-06-20 | DJ29-16 |  | <0.009 | clear | 219 | 816 | none | 8.22 | none | 0.14 | 0 | 0
Zone1 - South District, New Harbours | 2016-06-26 | DJ29-17 |  | <0.009 | clear | 218 | 827 | none | 8.19 | none | 0.26 | 0 | 0
Zone2-LL- Gibraltar Chronicle | 2016-06-26 | DJ29-18 |  | <0.009 | clear | 203 | 824 | none | 8.2 | none | 0.19 | 0 | 0
Zone3-ED- Highcliffe House | 2016-06-26 | DJ29-19 |  | <0.009 | clear | 216 | 859 | none | 8.2 | none | 0.18 | 0 | 0
Zone 4 - U R, Upper Galleries, tourist site kit | 2016-06-26 | DJ29-20 |  | <0.009 | clear | 226 | 880 | none | 8.18 | none | 0.14 | 0 | 0
Zone1 - Shipping, Distiller | 2016-07-05 | J30-1 |  | <0.009 | clear | 0.04 | 226 | none | 7.88 | none | 0.18 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2016-07-05 | J30-2 |  | <0.009 | clear | <0.01 | 199 | none | 7.94 | none | 0.24 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-07-05 | J30-3 |  | <0.009 | clear | 0.08 | 228 | none | 7.96 | none | 0.21 | 0 | 0
Zone 4 - UR, Lower Bruces Farm sampling tap | 2016-07-05 | J30-4 |  | <0.009 | clear | 0.01 | 237 | none | 7.9 | none | 0.17 | 0 | 0
Zone1 - High Level, Arengo's nursery | 2016-07-14 | J30-5 |  | <0.009 | clear | <0.01 | 194 | none | 8.24 | none | 0.11 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2016-07-14 | J30-6 |  | <0.009 | clear | 0.01 | 205 | none | 8.13 | none | 0.21 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-07-14 | J30-7 |  | <0.009 | clear | 0.08 | 206 | none | 8.25 | none | 0.1 | 0 | 0
Zone 4 - Poca Rocca | 2016-07-14 | J30-8 |  | <0.009 | clear | 0.04 | 231 | none | 8.23 | none | 0.16 | 0 | 0
Zone1 -Moorish Castle Estate | 2016-07-20 | J30-9 |  | <0.009 | clear | <0.01 | 207 | none | 6.82 | none | 0.26 | 0 | 0
Zone2- LL-Casemates | 2016-07-18 | J30-10 |  | <0.009 | clear | 0.11 | 206 | none | 8.04 | none | 0.41 | 0 | 0
Zone3-ED- Highcliffe House | 2016-07-20 | J30-11 |  | <0.009 | clear | 0.01 | 230 | none | 7.21 | none | 0.13 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2016-07-20 | J30-12 |  | <0.009 | clear | <0.01 | 238 | none | 7.25 | none | 0.31 | 0 | 0
Zone1 - North Front, Beachview Terraces | 2016-07-25 | J30-13 |  | <0.009 | clear | 0.04 | 210 | none | 7.96 | none | 0.13 | 0 | 0
Zone2-LL- Piaza | 2016-07-25 | J30-14 |  | <0.009 | clear | <0.01 | 208 | none | 7.85 | none | 0.45 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-07-27 | J30-15 |  | <0.009 | clear | 0.03 | 215 | none | 7.79 | none | 0.4 | 0 | 0
Zone 4 - MC Tourist Site | 2016-07-27 | J30-16 |  | <0.009 | clear | 0.03 | 220 | none | 7.86 | none | 0.16 | 0 | 0
Zone1 - South District, Ragged Staff Offices | 2016-08-03 | DA20-1 |  | <0.009 | clear | 212 | 771 | none | 7.93 | none | 0.12 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2016-08-03 | DA20-2 |  | <0.009 | clear | 213 | 735 | none | 7.77 | none | 0.26 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-08-03 | DA20-3 |  | <0.009 | clear | 234 | 735 | none | 8.02 | none | 0.2 | 0 | 0
Zone 4 - UR, Lower Bruces Farm sample tap | 2016-08-03 | DA20-4 |  | <0.009 | clear | 225 | 759 | none | 7.97 | none | 0.22 | 0 | 0
Zone1 - HL,Leanse Place, AquaGib M.Office | 2016-08-10 | DA20-5 |  | <0.009 | clear | 180 | 668 | none | 8.07 | none | 0.16 | 0 | 0
Zone2-LL- Gibraltar Chronicle | 2016-08-10 | DA20-6 |  | <0.009 | clear | 200 | 733 | none | 8.07 | none | 0.24 | 0 | 0
Zone3-ED- Highcliffe House | 2016-08-08 | DA20-7 |  | <0.009 | clear | 190 | 695 | none | 7.93 | none | 0.14 | 0 | 0
Zone 4 - Poca Rocca | 2016-08-10 | DA20-8 |  | <0.009 | clear | 191 | 680 | none | 8.09 | none | 0.13 | 0 | 0
Zone1 -Harbour Views | 2016-08-17 | DA20-9 |  | <0.009 | clear | 199 | 703 | none | 7.95 | none | 0.11 | 0 | 0
Zone2- LL- John Machintosh Hall | 2016-08-15 | DA20-10 |  | <0.009 | clear | 198 | 708 | none | 7.59 | none | 0.48 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-08-15 | DA20-11 |  | <0.009 | clear | 197 | 735 | none | 7.67 | none | 0.19 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2016-08-17 | DA20-12 |  | <0.009 | clear | 205 | 744 | none | 7.98 | none | 0.19 | 0 | 0
Zone1 - Moorish Castle Estate | 2016-08-24 | DA20-13 |  | <0.009 | clear | 179 | 742 | none | 7.99 | none | 0.18 | 0 | 0
Zone2-LL- Lesuire Centre | 2016-08-22 | DA20-14 |  | <0.009 | clear | 205 | 750 | none | 8 | none | 0.39 | 0 | 0
Zone3-ED- St. Bernards Church | 2016-08-22 | DA20-15 |  | <0.009 | clear | 180 | 709 | none | 8.05 | none | 0.26 | 0 | 0
Zone 4 - MC Tourist Site | 2016-08-24 | DA20-16 |  | <0.009 | clear | 195 | 715 | none | 8.05 | none | 0.18 | 0 | 0
Zone1 - North Front, Tercentenary Sports Hall | 2016-08-30 | DA20-17 |  | <0.009 | clear | 185 | 722 | none | 8.09 | none | 0.23 | 0 | 0
Zone2-LL- Casemates | 2016-09-01 | DA20-18 |  | <0.009 | clear | 202 | 771 | none | 7.9 | none | 0.41 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-09-01 | DA20-19 |  | <0.009 | clear | 207 | 794 | none | 7.98 | none | 0.17 | 0 | 0
Zone 4 - UR, Lower Bruces Farm sample tap | 2016-09-01 | DA20-20 |  | <0.009 | clear | 208 | 789 | none | 7.96 | none | 0.23 | 0 | 0
Zone1 - SD, New Harbours, Checkout Coviran | 2016-09-08 | DS10-1 |  | <0.009 | clear | 211 | 719 | none | 7.77 | none | 0.15 | 0 | 0
Zone2-LL- Piazza | 2016-09-08 | DS10-2 |  | <0.009 | clear | 205 | 716 | none | 7.68 | none | 0.19 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-09-06 | DS10-3 |  | <0.009 | clear | 203 | 792 | none | 7.92 | none | 0.22 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2016-09-08 | DS10-4 |  | <0.009 | clear | 207 | 715 | none | 7.74 | none | 0.19 | 0 | 0
Zone1 - Westside, St Bernard's Hospital | 2016-09-14 | DS10-5 |  | <0.009 | clear | 205 | 744 | none | 8.1 | none | 0.1 | 0 | 0
Zone2-LL- Gib Oil, Line Wall Road | 2016-09-14 | DS10-6 |  | <0.009 | clear | 211 | 755 | none | 8.03 | none | 0.2 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-09-14 | DS10-7 |  | <0.009 | clear | 221 | 790 | none | 8.11 | none | 0.25 | 0 | 0
Zone 4 - Upper Galleries | 2016-09-14 | DS10-8 |  | <0.009 | clear | 205 | 762 | none | 8.09 | none | 0.31 | 0 | 0
Zone1 -High Level, Arengo's nursery | 2016-09-19 | DS10-9 |  | <0.009 | clear | 188 | 725 | none | 8.2 | none | 0.23 | 0 | 0
Zone2- LL- John Machintosh Hall | 2016-09-21 | DS10-10 |  | <0.009 | clear | 198 | 761 | none | 7.97 | none | 0.12 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-09-21 | DS10-11 |  | <0.009 | clear | 186 | 725 | none | 7.94 | none | 0.1 | 0 | 0
Zone 4 - U.R, Moorish Castle tourist site | 2016-09-21 | DS10-12 |  | <0.009 | clear | 184 | 718 | none | 8.06 | none | 0.15 | 0 | 0
Zone1 - MC Estate, Key Way House | 2016-09-29 | DS10-13 |  | <0.009 | clear | 193 | 725 | none | 7.87 | none | 0.13 | 0 | 0
Zone2-LL- Gibraltar Chronicle | 2016-09-29 | DS10-14 |  | <0.009 | clear | 199 | 729 | none | 7.97 | none | 0.18 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-09-29 | DS10-15 |  | <0.009 | clear | 198 | 750 | none | 7.9 | none | 0.16 | 0 | 0
Zone 4 - U.R, Lower Bruces farm | 2016-09-29 | DS10-16 |  | <0.009 | clear | 204 | 743 | none | 7.86 | none | 0.22 | 0 | 0
Zone1 - Nf, Mariola Stores, Cemetery Road | 2016-10-04 | DO10-1 |  | <0.009 | clear | 197 | 780 | none | 7.82 | none | 0.21 | 0 | 0
Zone2-LL- Piazza | 2016-10-04 | DO10-2 |  | <0.009 | clear | 203 | 741 | none | 7.95 | none | 0.22 | 0 | 0
Zone3-ED- Highcliffe House | 2016-10-06 | DO10-3 |  | <0.009 | clear | 226 | 824 | none | 7.85 | none | 0.11 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2016-10-04 | DO10-4 |  | <0.009 | clear | 201 | 790 | none | 7.96 | none | 0.11 | 0 | 0
Zone1 - SD, New Harbours, Gibtelecom | 2016-10-13 | DO10-5 |  | <0.009 | clear | 209 | 770 | none | 7.96 | none | 0.37 | 0 | 0
Zone2-LL- Kings Bastion Leisure Centre | 2016-10-13 | DO10-6 |  | <0.009 | clear | 198 | 766 | none | 7.98 | none | 0.17 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-10-13 | DO10-7 |  | <0.009 | clear | 231 | 831 | none | 7.94 | none | 0.18 | 0 | 0
Zone 4 - Moorish Castle, tourist site | 2016-10-13 | DO10-8 |  | <0.009 | clear | 208 | 819 | none | 7.93 | none | 0.18 | 0 | 0
Zone1 -Shipping, Flying Angel | 2016-10-19 | DO10-9 |  | 0.012 | clear | 203 | 786 | none | 8 | none | 0.19 | 0 | 0
Zone2- LL- Bristol Hotel | 2016-10-19 | DO10-10 |  | <0.009 | clear | 196 | 776 | none | 8.06 | none | 0.29 | 0 | 0
Zone3-ED- Sunset Close | 2016-10-19 | DO10-11 |  | <0.009 | clear | 201 | 802 | none | 8.02 | none | 0.09 | 0 | 0
Zone 4 - Upper rock, Devils Gap | 2016-10-19 | DO10-12 |  | <0.009 | clear | 207 | 800 | none | 7.99 | none | 0.32 | 0 | 0
Zone1 - Westside, Mediterranean Rowing club | 2016-10-26 | DO10-13 |  | <0.009 | clear | 200 | 780 | none | 8.16 | none | 0.17 | 0 | 0
Zone2-LL- Cloister Ramp | 2016-10-24 | DO10-14 |  | <0.009 | clear | 201 | 779 | none | 7.86 | none | 0.31 | 0 | 0
Zone3-ED- Blackwood Tower, Brympton | 2016-10-26 | DO10-15 |  | <0.009 | clear | 205 | 819 | none | 8.14 | none | 0.16 | 0 | 0
Zone 4 - Upper rock, St Michael's Cave | 2016-10-24 | DO10-16 |  | <0.009 | clear | 209 | 805 | none | 7.83 | none | 0.25 | 0 | 0
Zone1 - HL, Barley Hill Hse, Prince Ed Road | 2016-11-02 | DN10-1 |  | <0.009 | clear | 211 | 841 | none | 8.08 | none | 0.3 | 0 | 0
Zone2-LL- 329 Main Street | 2016-10-30 | DN10-2 |  | <0.009 | clear | 198 | 750 | none | 8.06 | none | 0.19 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-11-02 | DN10-3 |  | <0.009 | clear | 222 | 890 | none | 8.12 | none | 0.14 | 0 | 0
Zone 4 - Upper rock, Lower Bruces Farm | 2016-10-30 | DN10-4 |  | <0.009 | clear | 211 | 849 | none | 8.05 | none | 0.28 | 0 | 0
Zone1 - South District, Anderson House | 2016-11-09 | DN10-5 |  | <0.009 | clear | 206 | 793 | none | 8.01 | none | 0.19 | 0 | 0
Zone2-LL- Eureka Meat Stall, 74 Gov St | 2016-11-09 | DN10-6 |  | <0.009 | clear | 203 | 790 | none | 7.93 | none | 0.29 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-11-07 | DN10-7 |  | <0.009 | clear | 208 | 801 | none | 8.18 | none | 0.13 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2016-11-09 | DN10-8 |  | <0.009 | clear | 210 | 826 | none | 7.98 | none | 0.13 | 0 | 0
Zone1 - Moorish Castle Estate, Wall House | 2016-11-16 | DN10-9 |  | <0.009 | clear | 200 | 809 | none | 8.11 | none | 0.16 | 0 | 0
Zone2-LL- 10 Town Range | 2016-11-14 | DN10-10 |  | <0.009 | clear | 209 | 795 | none | 8.02 | none | 0.33 | 0 | 0
Zone3-ED-Ocean Views Mental Health Facility | 2016-11-16 | DN10-11 |  | <0.009 | clear | 206 | 827 | none | 8.18 | none | 0.15 | 0 | 0
Zone 4 - Moorish Castle tourist site | 2016-11-16 | DN10-12 |  | <0.009 | clear | 212 | 847 | none | 8.19 | none | 0.1 | 0 | 0
Zone1-NF,Motor Vehicle Test Ctre, E.Beach | 2016-11-21 | DN10-13 |  | <0.009 | clear | 209 | 808 | none | 8.06 | none | 0.19 | 0 | 0
Zone2-LL- College Lane, Sheriff AJ Elec Con | 2016-11-21 | DN10-14 |  | <0.009 | clear | 206 | 800 | none | 8.04 | none | 0.28 | 0 | 0
Zone3-ED- Highcliffe House | 2016-11-23 | DN10-15 |  | <0.009 | clear | 211 | 811 | none | 8.04 | none | 0.09 | 0 | 0
Zone 4 - Upper rock, Devil's Gap meter box | 2016-11-21 | DN10-16 |  | <0.009 | clear | 211 | 858 | none | 8.05 | none | 0.31 | 0 | 0
Zone1 - Shipping, Cruise Terminal | 2016-11-29 | DN10-17 |  | <0.009 | clear | 200 | 805 | none | 8.18 | none | 0.2 | 0 | 0
Zone2-LL- Fish Market Lane | 2016-11-29 | DN10-18 |  | <0.009 | clear | 198 | 806 | none | 8.23 | none | 0.28 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-12-01 | DN10-19 |  | <0.009 | clear | 208 | 815 | none | 7.98 | none | 0.25 | 0 | 0
Zone 4 - Upper rock, St Michael's Cave | 2016-11-29 | DN10-20 |  | <0.009 | clear | 186 | 798 | none | 8.13 | none | 0.31 | 0 | 0
Zone1 - Westside, Mons Calpe Mews | 2016-12-08 | DD10-1 |  | <0.009 | clear | 196 | 802 | none | 8.12 | none | 0.14 | 0 | 0
Zone2-LL- Casemates | 2016-12-08 | DD10-2 |  | <0.009 | clear | 190 | 769 | none | 8.15 | none | 0.3 | 0 | 0
Zone3-ED- Highcliffe House | 2016-12-06 | DD10-3 |  | <0.009 | clear | 198 | 792 | none | 8.28 | none | 0.14 | 0 | 0
Zone 4 - UR,Lower Bruces Farm sample tap | 2016-12-08 | DD10-4 |  | <0.009 | clear | 197 | 828 | none | 8.11 | none | 0.16 | 0 | 0
Zone1 - High Level, 29 Flat Bastion Road | 2016-12-12 | DD10-5 |  | <0.009 | clear | 191 | 755 | none | 8.05 | none | 0.17 | 0 | 0
Zone2-LL-Senior Citizens Social Club,29 T.Rg | 2016-12-12 | DD10-6 |  | <0.009 | clear | 183 | 797 | none | 7.94 | none | 0.28 | 0 | 0
Zone3-ED- Buena Vista Estate | 2016-12-14 | DD10-7 |  | <0.009 | clear | 211 | 867 | none | 8.05 | none | 0.16 | 0 | 0
Zone 4 - U.Rock, moorish castle tourist site | 2016-12-14 | DD10-8 |  | <0.009 | clear | 218 | 832 | none | 7.95 | none | 0.14 | 0 | 0
Zone1 - South District, Petroil, Rosia Road | 2016-12-20 | DD10-9 |  | <0.009 | clear | 190 | 787 | none | 8.23 | none | 0.1 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2016-12-20 | DD10-10 |  | <0.009 | clear | 193 | 791 | none | 8.14 | none | 0.21 | 0 | 0
Zone3-ED- Cliffton Mews | 2016-12-20 | DD10-11 |  | <0.009 | clear | 222 | 852 | none | 8.16 | none | 0.17 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2016-12-20 | DD10-12 |  | <0.009 | clear | 215 | 859 | none | 8.08 | none | 0.23 | 0 | 0
Zone1 - Moorish Castle, Tankerville | 2016-12-28 | DD10-13 |  | <0.009 | clear | 185 | 810 | none | 7.98 | none | 0.09 | 0 | 0
Zone2-LL- Gavinos Passage | 2016-12-28 | DD10-14 |  | <0.009 | clear | 207 | 834 | none | 7.83 | none | 0.23 | 0 | 0
Zone3-ED- Eliotts Battery | 2016-12-28 | DD10-15 |  | <0.009 | clear | 218 | 867 | none | 7.92 | none | 0.17 | 0 | 0
Zone 4 - Upper rock, Devil's Gap | 2016-12-28 | DD10-16 |  | <0.009 | clear | 212 | 863 | none | 7.98 | none | 0.12 | 0 | 0
Zone1 - North Front, Glacis | 2017-01-03 | DJ31-1 |  | <0.009 | clear | 194 | 744 | none | 8.01 | none | 0.1 | 0 | 0
Zone2-LL- Gibraltar Chronicle | 2017-01-03 | DJ31-2 |  | <0.009 | clear | 198 | 811 | none | 8.02 | none | 0.17 | 0 | 0
Zone3-ED- Buena Vista Estate | 2017-01-03 | DJ31-3 |  | <0.009 | clear | 206 | 837 | none | 7.99 | none | 0.22 | 0 | 0
Zone 4 - Upper rock, St Michael's Cave | 2017-01-05 | DJ31-4 |  | <0.009 | clear | 191 | 753 | none | 7.97 | none | 0.28 | 0 | 0
Zone 1- Shipping, North Mole Industrial Park | 2017-01-11 | DJ31-5 |  | <0.009 | clear | 191 | 765 | none | 8.24 | none | 0.21 | 0 | 0
Zone 2-LL- Engineer's Lane | 2017-01-11 | DJ31-6 |  | <0.009 | clear | 196 | 799 | none | 8.26 | none | 0.16 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-01-11 | DJ31-7 |  | <0.009 | clear | 198 | 821 | none | 8.29 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm tap | 2017-01-09 | DJ31-8 |  | <0.009 | clear | 201 | 820 | none | 8.22 | none | 0.13 | 0 | 0
Zone 1- South District, Fire & Rescue Service | 2017-01-16 | DJ31-9 |  | <0.009 | clear | 179 | 672 | none | 8.27 | none | 0.08 | 0 | 0
Zone 2-LL- ICC | 2017-01-16 | DJ31-10 |  | <0.009 | clear | 196 | 794 | none | 8.15 | none | 0.28 | 0 | 0
Zone 3-ED- Sunset Close | 2017-01-18 | DJ31-11 |  | <0.009 | clear | 193 | 788 | none | 8.24 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm ap | 2017-01-18 | DJ31-12 |  | <0.009 | clear | 191 | 856 | none | 8.08 | none | 0.12 | 0 | 0
Zone 1- Westside, Europort, McDonalds | 2017-01-25 | DJ31-13 |  | <0.009 | clear | 176 | 713 | none | 8.32 | none | 0.09 | 0 | 0
Zone 2-LL- Midtown Coach & Carpark | 2017-01-25 | DJ31-14 |  | <0.009 | clear | 178 | 700 | none | 8.34 | none | 0.19 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-01-23 | DJ31-15 |  | <0.009 | clear | 187 | 763 | none | 8.25 | none | 0.1 | 0 | 0
Zone 4- Upper rock, M.C tourist site office | 2017-01-25 | DJ31-16 |  | <0.009 | clear | 206 | 773 | none | 8.26 | none | 0.23 | 0 | 0
Zone1 - M.C Estate, Ollies Takeaway | 2017-02-01 | DF11-1 |  | <0.009 | clear | 199 | 818 | none | 7.85 | none | 0.19 | 0 | 0
Zone2-LL- 2 Chircardo's Passage | 2017-02-01 | DF11-2 |  | <0.009 | clear | 207 | 757 | none | 7.78 | none | 0.09 | 0 | 0
Zone3-ED- Highcliffe House | 2017-01-30 | DF11-3 |  | 0.009 | clear | 196 | 840 | none | 8.21 | none | 0.13 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2017-02-01 | DF11-4 |  | <0.009 | clear | 210 | 837 | none | 8.17 | none | 0.24 | 0 | 0
Zone 1- North Front, Cemetery office | 2017-02-06 | DF11-5 |  | <0.009 | clear | 169 | 732 | none | 8.2 | none | 0.27 | 0 | 0
Zone 2-LL- Gibraltar College, Line Wall Road | 2017-02-08 | DF11-6 |  | <0.009 | clear | 197 | 799 | none | 8.21 | none | 0.15 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-02-08 | DF11-7 |  | <0.009 | clear | 197 | 800 | none | 8.28 | none | 0.1 | 0 | 0
Zone 4- Devil's Gap | 2017-02-08 | DF11-8 |  | <0.009 | clear | 197 | 801 | none | 8.19 | none | 0.1 | 0 | 0
Zone 1- wp, Gibmaroc Ltd, North Mole Ind Prk | 2017-02-15 | DF11-9 |  | <0.009 | clear | 195 | 796 | none | 8.1 | none | 0.17 | 0 | 0
Zone 2-LL- Kings Bastion Leisure Centre | 2017-02-15 | DF11-10 |  | 0.027 | clear | 186 | 794 | none | 8.13 | none | 0.15 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-02-15 | DF11-11 |  | <0.009 | clear | 201 | 827 | none | 8.14 | none | 0.14 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2017-02-15 | DF11-12 |  | <0.009 | clear | 205 | 782 | none | 8.06 | none | 0.23 | 0 | 0
Zone 1- S.D, Heathfield House, U Witham's rd | 2017-02-22 | DF11-13 |  | <0.009 | clear | 193 | 779 | none | 8.1 | none | 0.17 | 0 | 0
Zone 2-LL- Gib Oil, Line Wall Road | 2017-02-22 | DF11-14 |  | <0.009 | clear | 187 | 791 | none | 8.12 | none | 0.11 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-02-20 | DF11-15 |  | <0.009 | clear | 219 | 875 | none | 8.29 | none | 0.13 | 0 | 0
Zone 4- Moorish Castle tourist site | 2017-02-22 | DF11-16 |  | <0.009 | clear | 190 | 794 | none | 8.13 | none | 0.13 | 0 | 0
Zone1 - Westside, GASA Swimming Pool | 2017-03-01 | DM21-1 |  | <0.009 | clear | 185 | 751 | none | 8.03 | none | 0.1 | 0 | 0
Zone2-LL- Piazza | 2017-02-27 | DM21-2 |  | <0.009 | clear | 185 | 778 | none | 8.02 | none | 0.26 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-02-27 | DM21-3 |  | <0.009 | clear | 189 | 779 | none | 7.99 | none | 0.11 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2017-03-01 | DM21-4 |  | <0.009 | clear | 195 | 783 | none | 8.06 | none | 0.15 | 0 | 0
Zone 1- Moorish Castle Estate | 2017-03-07 | DM21-5 |  | <0.009 | clear | 184 | 746 | none | 8.17 | none | 0.13 | 0 | 0
Zone 2-LL- Piazza | 2017-03-07 | DM21-6 |  | <0.009 | clear | 189 | 770 | none | 8.17 | none | 0.13 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-03-07 | DM21-7 |  | <0.009 | clear | 194 | 780 | none | 8.21 | none | 0.1 | 0 | 0
Zone 4- Upper Rock, Poca Rocca | 2017-03-07 | DM21-8 |  | <0.009 | clear | 198 | 778 | none | 8.25 | none | 0.2 | 0 | 0
Zone 1- North Front, Laguna Est, Sortie Hse | 2017-03-15 | DM21-9 |  | <0.009 | clear | 193 | 767 | none | 7.99 | none | 0.09 | 0 | 0
Zone 2-LL- Pure Lighting, Ocean Heights | 2017-03-15 | DM21-10 |  | <0.009 | clear | 180 | 818 | none | 7.78 | none | 0.18 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-03-15 | DM21-11 |  | <0.009 | clear | 177 | 774 | none | 7.87 | none | 0.19 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2017-03-15 | DM21-12 |  | <0.009 | clear | 198 | 759 | none | 7.81 | none | 0.28 | 0 | 0
Zone 1- Shipping, M&E Depot AquaGib | 2017-03-20 | DM21-13 |  | <0.009 | clear | 171 | 733 | none | 7.9 | none | 0.16 | 0 | 0
Zone 2-LL-Gibraltar Regiment Club, Irish Town | 2017-03-22 | DM21-14 |  | <0.009 | clear | 187 | 753 | none | 7.82 | none | 0.3 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-03-22 | DM21-15 |  | <0.009 | clear | 200 | 787 | none | 7.84 | none | 0.17 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2017-03-22 | DM21-16 |  | <0.009 | clear | 198 | 772 | none | 7.86 | none | 0.11 | 0 | 0
Zone1 - Westside, N.Mole Rd, Gib Carparks | 2017-04-05 | DA21-1 |  | <0.009 | clear | 167 | 748 | none | 7.91 | none | 0.16 | 0 | 0
Zone2-LL- Cornwall's Centre, Cheers | 2017-04-05 | DA21-2 |  | <0.009 | clear | 191 | 750 | none | 7.88 | none | 0.13 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-04-03 | DA21-3 |  | <0.009 | clear | 181 | 759 | none | 7.92 | none | 0.15 | 0 | 0
Zone 4 - Upper rock, Poca Rocca | 2017-04-03 | DA21-4 |  | <0.009 | clear | 190 | 758 | none | 7.93 | none | 0.11 | 0 | 0
Zone 1- Moorish Castle Estate | 2017-04-11 | DA21-5 |  | <0.009 | clear | 209 | 435 | none | 7.91 | none | 0.27 | 0 | 0
Zone 2-LL- Piazza | 2017-04-11 | DA21-6 |  | <0.009 | clear | 197 | 735 | none | 7.9 | none | 0.15 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-04-11 | DA21-7 |  | <0.009 | clear | 191 | 813 | none | 7.87 | none | 0.18 | 0 | 0
Zone 4- Poca Rocca | 2017-04-11 | DA21-8 |  | <0.009 | clear | 224 | 819 | none | 7.96 | none | 0.11 | 0 | 0
Zone 1- North Front, Car Car Centre | 2017-04-20 | DA21-9 |  | <0.009 | clear | 184 | 789 | none | 8.39 | none | 0.3 | 0 | 0
Zone 2-LL- ICC | 2017-04-20 | DA21-10 |  | <0.009 | clear | 163 | 764 | none | 8.3 | none | 0.16 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-04-20 | DA21-11 |  | <0.009 | clear | 210 | 871 | none | 8.37 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Moorish Castle tourist site | 2017-04-20 | DA21-12 |  | <0.009 | clear | 184 | 835 | none | 8.29 | none | 0.1 | 0 | 0
Zone 1- Shipping, Gib Elec | 2017-04-24 | DA21-13 |  | <0.009 | clear | 201 | 774 | none | 8.24 | none | 0.28 | 0 | 0
Zone 2-LL- Line Wall Road, Gibraltar Chronicle | 2017-04-24 | DA21-14 |  | 0.018 | clear | 199 | 762 | none | 8.2 | none | 0.1 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-04-24 | DA21-15 |  | <0.009 | clear | 179 | 824 | none | 8.29 | none | 0.19 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2017-04-24 | DA21-16 |  | <0.009 | clear | 187 | 836 | none | 8.29 | none | 0.19 | 0 | 0
Zone1 - South District, Ragged Staff | 2017-05-02 | DM22-1 |  | <0.009 | clear | 198 | 800 | none | 8.07 | none | 0.21 | 0 | 0
Zone2-LL- Casemates toilets | 2017-05-02 | DM22-2 |  | <0.009 | clear | 189 | 769 | none | 8.1 | none | 0.36 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-05-02 | DM22-3 |  | <0.009 | clear | 210 | 825 | none | 8.28 | none | 0.19 | 0 | 0
Zone 4 - Upper rock, Upper Galleries | 2017-05-02 | DM22-4 |  | <0.009 | clear | 213 | 824 | none | 8.36 | none | 0.1 | 0 | 0
Zone 1- Westside, Timeout Cafe | 2017-05-09 | DM22-5 |  | <0.009 | clear | 189 | 791 | none | 8.12 | none | 0.09 | 0 | 0
Zone 2-LL- John Mackintosh Hall | 2017-05-09 | DM22-6 |  | <0.009 | clear | 172 | 775 | none | 8.2 | none | 0.19 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-05-11 | DM22-7 |  | <0.009 | clear | 185 | 768 | none | 7.85 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2017-05-11 | DM22-8 |  | <0.009 | clear | 191 | 786 | none | 7.87 | none | 0.22 | 0 | 0
Zone 1- Moorish Castle Estate | 2017-05-18 | DM22-9 |  | <0.009 | clear | 186 | 778 | none | 8.02 | none | 0.13 | 0 | 0
Zone 2-LL- Royal Gib Regiment .... | 2017-05-18 | DM22-10 |  | <0.009 | clear | 207 | 773 | none | 7.77 | none | 0.09 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-05-18 | DM22-11 |  | <0.009 | clear | 201 | 813 | none | 7.78 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Hays Level, WWII Tunnels | 2017-05-18 | DM22-12 |  | <0.009 | clear | 198 | 782 | none | 7.93 | none | 0.21 | 0 | 0
Zone 1- North Front, MOT Centre | 2017-05-24 | DM22-13 |  | <0.009 | clear | 190 | 792 | none | 7.93 | none | 0.19 | 0 | 0
Zone 2-LL- Casemates | 2017-05-22 | DM22-14 |  | <0.009 | clear | 241 | 771 | none | 8.09 | none | 0.18 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-05-24 | DM22-15 |  | <0.009 | clear | 241 | 784 | none | 7.98 | none | 0.21 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2017-05-22 | DM22-16 |  | <0.009 | clear | 210 | 802 | none | 8.06 | none | 0.17 | 0 | 0
Zone 1- Shipping, AquaGib, Mech. Eng dpt | 2017-06-07 | DJ32-5 |  | <0.009 | clear | 211 | 825 | none | 7.83 | none | 0.1 | 0 | 0
Zone 2-LL- ICC | 2017-06-07 | DJ32-6 |  | <0.009 | clear | 210 | 802 | none | 7.87 | none | 0.18 | 0 | 0
Zone 3-ED- Elliots Battery | 2017-06-07 | DJ32-7 |  | <0.009 | clear | 236 | 845 | none | 7.91 | none | 0.23 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2017-06-07 | DJ32-8 |  | <0.009 | clear | 223 | 835 | none | 7.96 | none | 0.12 | 0 | 0
Zone 1- South District, New Harbours | 2017-06-14 | DJ32-9 |  | <0.009 | clear | 196 | 801 | none | 8.05 | none | 0.1 | 0 | 0
Zone 2-LL- Kings Bastion | 2017-06-14 | DJ32-10 |  | <0.009 | clear | 232 | 793 | none | 8.15 | none | 0.1 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-06-14 | DJ32-11 |  | <0.009 | clear | 191 | 817 | none | 8.06 | none | 0.19 | 0 | 0
Zone 4- Upper rock, Moorish Castle tourist site | 2017-06-12 | DJ32-12 |  | <0.009 | clear | 242 | 829 | none | 7.9 | none | 0.17 | 0 | 0
Zone 1- Westside, McDonalds | 2017-06-20 | DJ32-13 |  | <0.009 | clear | 240 | 852 | none | 7.92 | none | 0.09 | 0 | 0
Zone 2-LL- Gibraltar College | 2017-06-20 | DJ32-14 |  | <0.009 | clear | 212 | 803 | none | 8.09 | none | 0.18 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-06-20 | DJ32-15 |  | <0.009 | clear | 227 | 881 | none | 8.2 | none | 0.1 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2017-06-20 | DJ32-16 |  | <0.009 | clear | 239 | 868 | none | 8.18 | none | 0.24 | 0 | 0
Zone 1- Moorish Castle Est, Ollie's Takeaway | 2017-06-28 | DJ32-17 |  | <0.009 | clear | 211 | 811 | none | 7.83 | none | 0.13 | 0 | 0
Zone 2-LL- Pizza | 2017-06-26 | DJ32-18 |  | <0.009 | clear | 196 | 841 | none | 8.08 | none | 0.17 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-06-28 | DJ32-19 |  | <0.009 | clear | 202 | 828 | none | 8.09 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2017-06-28 | DJ32-20 |  | <0.009 | clear | 229 | 801 | none | 8.03 | none | 0.18 | 0 | 0
Zone1 - North Front, Beach View Terraces | 2017-07-03 | DJ33-1 |  | <0.009 | clear | 223 | 719 | none | 7.89 | none | 0.18 | 0 | 0
Zone2-LL- Gib Chronicle | 2017-07-03 | DJ33-2 |  | <0.009 | clear | 219 | 802 | none | 7.9 | none | 0.15 | 0 | 0
Zone 3-ED- Elliots Battery | 2017-07-05 | DJ33-3 |  | <0.009 | clear | 206 | 812 | none | 8.19 | none | 0.09 | 0 | 0
Zone 4 - Upper Rock, Devils Gap | 2017-07-05 | DJ33-4 |  | <0.009 | clear | 194 | 790 | none | 8.23 | none | 0.16 | 0 | 0
Zone 1- Shipping, AquaGib, M & Eng dept | 2017-07-12 | DJ33-5 |  | <0.009 | clear | 150 | 765 | none | 8.12 | none | 0.17 | 0 | 0
Zone 2-LL- ICC | 2017-07-12 | DJ33-6 |  | <0.009 | clear | 188 | 790 | none | 8.16 | none | 0.18 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-07-10 | DJ33-7 |  | <0.009 | clear | 231 | 849 | none | 7.75 | none | 0.15 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2017-07-12 | DJ33-8 |  | <0.009 | clear | 185 | 814 | none | 8.35 | none | 0.08 | 0 | 0
Zone 1- South District,Interbuild, New Harbours | 2017-07-19 | DJ33-9 |  | <0.009 | clear | 217 | 845 | none | 7.72 | none | 0.1 | 0 | 0
Zone 2-LL- Kings Bastion | 2017-07-19 | DJ33-10 |  | <0.009 | clear | 226 | 828 | none | 7.79 | none | 0.15 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-07-19 | DJ33-11 |  | <0.009 | clear | 235 | 853 | none | 7.8 | none | 0.14 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2017-07-19 | DJ33-12 |  | <0.009 | clear | 242 | 831 | none | 7.93 | none | 0.17 | 0 | 0
Zone 1- High Level, Arengo's Nursery | 2017-07-26 | DJ33-13 |  | <0.009 | clear | 183 | 789 | none | 8.01 | none | 0.12 | 0 | 0
Zone 2-LL- Casmates | 2017-07-26 | DJ33-14 |  | <0.009 | clear | 176 | 794 | none | 8.11 | none | 0.11 | 0 | 0
Zone 3-ED- Elliots Battery | 2017-07-26 | DJ33-15 |  | 0.009 | clear | 189 | 805 | none | 8.06 | none | 0.18 | 0 | 0
Zone 4- Upper rock,MC Tourist Site | 2017-07-26 | DJ33-16 |  | <0.009 | clear | 189 | 839 | none | 8.01 | none | 0.22 | 0 | 0
Zone1 - Westside | 2017-07-31 | DA22-1 |  | <0.009 | clear | 177 | 816 | none | 7.76 | none | 0.18 | 0 | 0
Zone2-LL- Engineer's Lane, Continental Hotel | 2017-07-31 | DA22-2 |  | <0.009 | clear | 186 | 833 | none | 7.78 | none | 0.15 | 0 | 0
Zone 3-ED- Lynx FC | 2017-07-31 | DA22-3 |  | <0.009 | clear | 202 | 856 | none | 7.81 | none | 0.12 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2017-07-31 | DA22-4 |  | <0.009 | clear | 193 | 839 | none | 7.67 | none | 0.07 | 0 | 0
Zone 1- 10 MacMillan House, M.C Estate. | 2017-08-09 | DA22-5 |  | <0.009 | clear | 199 | 812 | none | 7.7 | none | 0.11 | 0 | 0
Zone 2-LL- Piazza | 2017-08-09 | DA22-6 |  | <0.009 | clear | 240 | 846 | none | 7.69 | none | 0.13 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-08-09 | DA22-7 |  | <0.009 | clear | 226 | 871 | none | 7.78 | none | 0.14 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2017-08-09 | DA22-8 |  | <0.009 | clear | 221 | 862 | none | 7.78 | none | 0.12 | 0 | 0
Zone1 NF,Eastern Beach, Lifeguard South Pst | 2017-08-16 | DA22-9 |  | <0.009 | clear | 172 | 795 | none | 7.92 | none | 0.14 | 0 | 0
Zone 2-LL- Midtown Dev, Coach Park | 2017-08-14 | DA22-10 |  | <0.009 | clear | 197 | 809 | none | 7.94 | none | 0.1 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-08-14 | DA22-11 |  | <0.009 | clear | 203 | 826 | none | 8.13 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Devils Gap | 2017-08-16 | DA22-12 |  | <0.009 | clear | 188 | 848 | none | 7.92 | none | 0.07 | 0 | 0
Zone 1- Shipping | 2017-08-21 | DA22-13 |  | <0.009 | clear | 194 | 787 | none | 7.73 | none | 0.14 | 0 | 0
Zone 2-LL- ICC | 2017-08-21 | DA22-14 |  | <0.009 | clear | 188 | 766 | none | 7.7 | none | 0.32 | 0 | 0
Zone 3-ED- Buena Vista | 2017-08-21 | DA22-15 |  | <0.009 | clear | 190 | 732 | none | 7.77 | none | 0.12 | 0 | 0
Zone 4- Upper rock, WWll Tunnels | 2017-08-23 | DA22-16 |  | <0.009 | clear | 195 | 808 | none | 8.05 | none | 0.13 | 0 | 0
Zone 1- Alameda Kiosk | 2017-08-29 | DA22-13 |  | <0.009 | clear | 218 | 841 | none | 8.06 | none | 0.09 | 0 | 0
Zone 2-LL- Mackintosh Hall | 2017-08-29 | DA22-14 |  | <0.009 | clear | 217 | 804 | none | 7.91 | none | 0.16 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-08-29 | DA22-15 |  | <0.009 | clear | 225 | 861 | none | 8.07 | none | 0.09 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2017-08-31 | DA22-16 |  | <0.009 | clear | 201 | 857 | none | 7.82 | none | 0.19 | 0 | 0
Zone1-HL,39 Town Range, Senior CitizensClub | 2017-09-07 | DS11-1 |  | <0.009 | clear | 201 | 823 | none | 8.08 | none | 0.13 | 0 | 0
Zone2-LL- Kings Bastion Lesiure Centre | 2017-09-07 | DS11-2 |  | <0.009 | clear | 196 | 827 | none | 8.1 | none | 0.21 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-09-05 | DS11-3 |  | <0.009 | clear | 178 | 807 | none | 7.82 | none | 0.13 | 0 | 0
Zone 4 - Upper Rock, MC tourist site | 2017-09-05 | DS11-4 |  | <0.009 | clear | 210 | 844 | none | 7.77 | none | 0.09 | 0 | 0
Zone 1- Westside, Europort, The Lunchbox | 2017-09-13 | DS11-5 |  | <0.009 | clear | 196 | 721 | none | 8.18 | none | 0.11 | 0 | 0
Zone 2-LL- The Gibraltar College | 2017-09-13 | DS11-6 |  | <0.009 | clear | 192 | 820 | none | 8.14 | none | 0.18 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-09-13 | DS11-7 |  | <0.009 | clear | 185 | 786 | none | 8.2 | none | 0.24 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2017-09-13 | DS11-8 |  | <0.009 | clear | 200 | 750 | none | 8.22 | none | 0.07 | 0 | 0
Zone 1- Moorish Castle Estate, 1 Calpe House | 2017-09-20 | DS11-9 |  | <0.009 | clear | 184 | 779 | none | 7.88 | none | 0.15 | 0 | 0
Zone 2-LL- Gib Oil, Line Wall Road | 2017-09-20 | DS11-10 |  | <0.009 | clear | 208 | 809 | none | 7.93 | none | 0.17 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-09-18 | DS11-11 |  | <0.009 | clear | 211 | 778 | none | 8.03 | none | 0.19 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2017-09-20 | DS11-12 |  | <0.009 | clear | 186 | 773 | none | 7.85 | none | 0.1 | 0 | 0
Zone 1- North Front, Bayside School | 2017-09-28 | DS11-13 |  | <0.009 | clear | 176 | 763 | none | 7.93 | none | 0.11 | 0 | 0
Zone 2-LL- R Gib Reg Association, IrishTown | 2017-09-28 | DS11-14 |  | <0.009 | clear | 191 | 780 | none | 8.09 | none | 0.18 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-09-28 | DS11-15 |  | <0.009 | clear | 182 | 761 | none | 8.15 | none | 0.21 | 0 | 0
Zone 4- Upper rock, Devils Gap | 2017-09-28 | DS11-16 |  | <0.009 | clear | 186 | 777 | none | 8.12 | none | 0.09 | 0 | 0
Zone1-SD, 57 Knight's Crt, Upper Witham's Rd | 2017-10-02 | DO11-1 |  | <0.009 | clear | 203 | 756 | none | 7.77 | none | 0.16 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-10-02 | DO11-2 |  | <0.009 | clear | 199 | 757 | none | 7.62 | none | 0.23 | 0 | 0
Zone 1- High Level, 29 Flat Bastion Road | 2017-10-11 | DO11-3 |  | <0.009 | clear | 209 | 780 | none | 7.99 | none | 0.14 | 0 | 0
Zone 2-LL- Gib Oil, Line Wall Road | 2017-10-11 | DO11-4 |  | <0.009 | clear | 220 | 813 | none | 7.95 | none | 0.1 | 0 | 0
Zone 3-ED- Cliffton Mews | 2017-10-11 | DO11-5 |  | <0.009 | clear | 218 | 850 | none | 7.97 | none | 0.24 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2017-10-11 | DO11-6 |  | <0.009 | clear | 205 | 827 | none | 7.99 | none | 0.09 | 0 | 0
Zone1- Westside, Gibraltar Car Parks Ltd 45 North Mole Road | 2017-10-18 | DO11-7 |  | <0.009 | clear | 209 | 840 | none | 8.07 | none | 0.2 | 0 | 0
Zone2-Low Level- Gibraltar Chronicle, Watergate House, Casemates Square | 2017-10-18 | DO11-8 |  | <0.009 | clear | 197 | 817 | none | 8.1 | none | 0.09 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-10-18 | DO11-9 |  | <0.009 | clear | 183 | 832 | none | 8.08 | none | 0.15 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2017-10-16 | DO11-10 |  | <0.009 | clear | 212 | 831 | none | 8.04 | none | 0.14 | 0 | 0
Zone1- Moorish Castle Estate ( 12 Keightley House) | 2017-10-23 | DO11-11 |  | <0.009 | clear | 223 | 810 | none | 7.99 | none | 0.09 | 0 | 0
Zone 2-Low Level - 36 Macintosh Square, La Charcuterie | 2017-10-23 | DO11-12 |  | <0.009 | clear | 219 | 802 | none | 8 | none | 0.12 | 0 | 0
Zone 3-ED- Highcliffe House | 2017-10-23 | DO11-13 |  | <0.009 | clear | 210 | 841 | none | 7.93 | none | 0.18 | 0 | 0
Zone 4- Upper rock, Poca Roca filter room | 2017-10-23 | DO11-14 |  | <0.009 | clear | 209 | 839 | none | 7.96 | none | 0.14 | 0 | 0
Zone1 - Shipping, Coviran, Waterport Terraces, Waterport Wharf | 2017-10-29 | DN11-1 |  | <0.009 | clear | 209 | 768 | none | 8.05 | none | 0.16 | 0 | 0
Zone2-LL- Bristol Hotel | 2017-10-29 | DN11-2 |  | <0.009 | clear | 215 | 826 | none | 8.09 | none | 0.12 | 0 | 0
Zone 3-ED- Europa Point public toilets | 2017-10-29 | DN11-3 |  | <0.009 | clear | 243 | 910 | none | 8.16 | none | 0.18 | 0 | 0
Zone 4 - Upper Rock, Devil's Gap | 2017-10-29 | DN11-4 |  | <0.009 | clear | 235 | 865 | none | 8.15 | none | 0.14 | 0 | 0
Zone 1- South District, Gibelec, Rosia Road | 2017-11-06 | DN11-5 |  | <0.009 | clear | 217 | 820 | none | 8.13 | none | 0.15 | 0 | 0
Zone 2-LL- Mackintosh Hall | 2017-11-10 | DN11-6 |  | <0.009 | clear | 217 | 822 | none | 8.14 | none | 0.49 | 0 | 0
Zone 3-ED- Sunset Close | 2017-11-10 | DN11-7 |  | <0.009 | clear | 219 | 845 | none | 8.19 | none | 0.23 | 0 | 0
Zone 4- Upper rock, Poca Roca filter room | 2017-11-10 | DN11-8 |  | <0.009 | clear | 227 | 860 | none | 8.2 | none | 0.28 | 0 | 0
Zone 1- North Front, Catalan Bay, Village Inn toilet | 2017-11-14 | DN11-9 |  | <0.009 | clear | 203 | 776 | none | 8.23 | none | 0.21 | 0 | 0
Zone 2-LL- ICC toilets | 2017-11-14 | DN11-10 |  | <0.009 | clear | 217 | 827 | none | 8.15 | none | 0.22 | 0 | 0
Zone 3-ED- The Clifftons | 2017-11-14 | DN11-11 |  | <0.009 | clear | 209 | 794 | none | 8.17 | none | 0.2 | 0 | 0
Zone 4- Upper rock, Upper Galleries toilets | 2017-11-14 | DN11-12 |  | <0.009 | clear | 221 | 824 | none | 8.2 | none | 0.24 | 0 | 0
Zone 1- High Level, Arengos, Little Learners nursery | 2017-11-22 | DN11-13 |  | <0.009 | clear | 193 | 761 | none | 8.22 | none | 0.11 | 0 | 0
Zone 2-LL- Kings Bastion Leisure Centre | 2017-11-20 | DN11-14 |  | 0.01 | clear | 196 | 718 | none | 8.42 | none | 0.25 | 0 | 0
Zone 3-ED- Eliotts Battery | 2017-11-20 | DN11-15 |  | <0.009 | clear | 175 | 670 | none | 8.07 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Moorish castle tourist site | 2017-11-22 | DN11-16 |  | <0.009 | clear | 198 | 725 | none | 8.07 | none | 0.19 | 0 | 0
Zone1 - Moorish Castle Estate, 12 MacMillan House | 2017-12-04 | DD11-1 |  | <0.009 | clear | 212 | 789 | none | 8.1 | none | 0.21 | 0 | 0
Zone2 - Low Level - Casemates Square | 2017-12-06 | DD11-2 |  | <0.009 | clear | 218 | 779 | none | 7.77 | none | 0.21 | 0 | 0
Zone 3 - Europa District - Cliffton Mews | 2017-12-04 | DD11-3 |  | <0.009 | clear | 202 | 810 | none | 8.1 | none | 0.15 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2017-12-06 | DD11-4 |  | <0.009 | clear | 203 | 789 | none | 7.97 | none | 0.17 | 0 | 0
Zone 1- Shipping, Care Agency, North Mole Road | 2017-12-11 | DD11-5 |  | 0.017 | clear | 215 | 787 | none | 7.87 | none | 0.19 | 0 | 0
Zone 2 - Low Level - ICC toilets | 2017-12-11 | DD11-6 |  | <0.009 | clear | 209 | 809 | none | 7.94 | none | 0.17 | 0 | 0
Zone 3 - Europa District - Eliotts Battery | 2017-12-11 | DD11-7 |  | <0.009 | clear | 217 | 815 | none | 7.98 | none | 0.25 | 0 | 0
Zone 4- Upper rock, Devil's Gap meter box | 2017-12-13 | DD11-8 |  | <0.009 | clear | 213 | 815 | none | 8.19 | none | 0.11 | 0 | 0
Zone 1- South District, AquaGib, Ragged Staff depot | 2017-12-19 | DD11-9 |  | <0.009 | clear | 208 | 784 | none | 7.79 | none | 0.19 | 0 | 0
Zone 2- Low Level - 89 Governor's Street | 2017-12-19 | DD11-10 |  | <0.009 | clear | 179 | 803 | none | 7.81 | none | 0.14 | 0 | 0
Zone 3- Europa District- Highcliffe House | 2017-12-19 | DD11-11 |  | <0.009 | clear | 203 | 766 | none | 7.87 | none | 0.22 | 0 | 0
Zone 4- Upper rock, Upper Galleries toilets | 2017-12-19 | DD11-12 |  | <0.009 | clear | 222 | 812 | none | 7.12 | none | 0.17 | 0 | 0
Zone 1- North Front, Beach View Terraces | 2017-12-27 | DD11-13 |  | 0.011 | clear | 198 | 765 | none | 8.29 | none | 0.27 | 0 | 0
Zone 2- Low Level - Gib Oil, Line Wall Road | 2017-12-27 | DD11-14 |  | 0.01 | clear | 206 | 795 | none | 8.19 | none | 0.13 | 0 | 0
Zone 3- Europa District - Cliffton Mews | 2017-12-27 | DD11-15 |  | <0.009 | clear | 193 | 720 | none | 8.2 | none | 0.15 | 0 | 0
Zone 4- Upper Rock, Moorish Castle tourist site | 2017-12-27 | DD11-16 |  | 0.01 | clear | 196 | 773 | none | 8.16 | none | 0.11 | 0 | 0
Zone1- High Level, St Jagos Estate | 2018-01-04 | DJ34-1 |  | 0.013 | clear | 184 | 784 | none | 8.7 | none | 0.18 | 0 | 0
Zone2- Low Level - Piazza | 2018-01-04 | DJ34-2 |  | <0.009 | clear | 217 | 786 | none | 8.46 | none | 0.09 | 0 | 0
Zone 3- Europa District - Eliotts Battery | 2018-01-04 | DJ34-3 |  | <0.009 | clear | 216 | 785 | none | 8.4 | none | 0.12 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2018-01-02 | DJ34-4 |  | <0.009 | clear | 208 | 771 | none | 8.5 | none | 0.23 | 0 | 0
Zone 1- Westside, Acquitania House, Varyl Begg Estate | 2018-01-09 | DJ34-5 |  | <0.009 | clear | 196 | 764 | none | 8.19 | none | 0.11 | 0 | 0
Zone 2- Low Level - Gibraltar College | 2018-01-09 | DJ34-6 |  | <0.009 | clear | 213 | 836 | none | 8.2 | none | 0.18 | 0 | 0
Zone 3- Europa District- Highcliffe House | 2018-01-09 | DJ34-7 |  | <0.009 | clear | 220 | 844 | none | 8.17 | none | 0.23 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2018-01-09 | DJ34-8 |  | <0.009 | clear | 223 | 847 | none | 8.07 | none | 0.1 | 0 | 0
Zone 1- Moorish Castle Estate, 29 Ince House | 2018-01-17 | DJ34-9 |  | <0.009 | clear | 201 | 825 | none | 8.34 | none | 0.23 | 0 | 0
Zone 2- Low Level- Secretary's Lane, Civil Status & Reg Office | 2018-01-17 | DJ34-10 |  | 0.01 | clear | 231 | 815 | none | 8.27 | none | 0.1 | 0 | 0
Zone 3- Europa District- Cliffton Mews | 2018-01-17 | DJ34-11 |  | <0.009 | clear | 240 | 831 | none | 8.18 | none | 0.16 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2018-01-17 | DJ34-12 |  | <0.009 | clear | 223 | 853 | none | 8.24 | none | 0.13 | 0 | 0
Zone 1- Shipping, Cruise Terminal | 2018-01-22 | DJ34-13 |  | <0.009 | clear | 238 | 848 | none | 8.07 | none | 0.24 | 0 | 0
Zone 2- Low Level - 20A Engineers's Lane | 2018-01-22 | DJ34-14 |  | <0.009 | clear | 221 | 829 | none | 8.09 | none | 0.19 | 0 | 0
Zone 3- Europa District - Eliotts Battery | 2018-01-22 | DJ34-15 |  | <0.009 | clear | 229 | 926 | none | 8.05 | none | 0.08 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-01-22 | DJ34-16 |  | <0.009 | clear | 206 | 862 | none | 8.12 | none | 0.15 | 0 | 0
Zone 1- North Front, Beach View Terraces | 2018-01-29 | DJ34-17 |  | 0.01 | clear | 208 | 803 | none | 8.26 | none | 0.26 | 0 | 0
Zone 2-Low Level - 39 Town Range, Senior Citizens Social Club | 2018-01-31 | DJ34-18 |  | <0.009 | clear | 196 | 845 | none | 7.75 | none | 0.13 | 0 | 0
Zone 3-Europa District- Europa Express, Europa Point | 2018-01-29 | DJ34-19 |  | <0.009 | clear | 224 | 812 | none | 8.23 | none | 0.18 | 0 | 0
Zone 4- Upper Rock, Moorish Castle tourist site | 2018-01-31 | DJ34-20 |  | 0.013 | clear | 194 | 775 | none | 7.84 | none | 0.19 | 0 | 0
Zone 1- South District, 30 Roger's Road | 2018-02-05 | DF12-1 |  | <0.009 | clear | 209 | 796 | none | 8.17 | none | 0.13 | 0 | 0
Zone2-LL-Gibraltar Chronicle,Watergate Hse, Casemates Square | 2018-02-07 | DF12-2 |  | 0.01 | clear | 234 | 797 | none | 8.07 | none | 0.13 | 0 | 0
Zone 3-Europa District- Highcliffe House | 2018-02-05 | DF12-3 |  | 0.013 | clear | 207 | 821 | none | 8.12 | none | 0.2 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2018-02-05 | DF12-4 |  | <0.009 | clear | 214 | 802 | none | 8.15 | none | 0.17 | 0 | 0
Zone 1-North Front, D& V Licensing Dept, 4-6 Eastern Beach Rd | 2018-02-12 | DF12-5 |  | <0.009 | clear | 229 | 766 | none | 8.2 | none | 0.19 | 0 | 0
Zone 2-Low Level - Piazza | 2018-02-12 | DF12-6 |  | <0.009 | clear | 202 | 790 | none | 8.47 | none | 0.21 | 0 | 0
Zone 3-Europa District- Cliffton Mews | 2018-02-12 | DF12-7 |  | <0.009 | clear | 198 | 745 | none | 8.45 | none | 0.16 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2018-02-12 | DF12-8 |  | <0.009 | clear | 171 | 765 | none | 8.59 | none | 0.14 | 0 | 0
Zone 1- High Level, 61 Prince Edward's Road, Flat 19 | 2018-02-21 | DF12-9 |  | <0.009 | clear | 215 | 781 | none | 8.1 | none | 0.1 | 0 | 0
Zone 2-Low Level - John Mackintosh Hall | 2018-02-21 | DF12-10 |  | 0.01 | clear | 207 | 768 | none | 8.09 | none | 0.21 | 0 | 0
Zone 3-Europa District - Eliotts Battery | 2018-02-21 | DF12-11 |  | <0.009 | clear | 197 | 765 | none | 8.06 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2018-02-21 | DF12-12 |  | 0.015 | clear | 199 | 783 | none | 8.11 | none | 0.22 | 0 | 0
Zone 1- Moorish Castle Estate, Ollie's Takeaway | 2018-02-26 | DF12-13 |  | <0.009 | clear | 189 | 762 | none | 8.3 | none | 0.23 | 0 | 0
Zone 2-Low Level- Gavino's Passage | 2018-02-26 | DF12-14 |  | <0.009 | clear | 186 | 773 | none | 8.23 | none | 0.13 | 0 | 0
Zone 3-Europa District- Highcliffe House | 2018-02-26 | DF12-15 |  | <0.009 | clear | 193 | 754 | none | 8.27 | none | 0.16 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-02-26 | DF12-16 |  | <0.009 | clear | 184 | 759 | none | 8.29 | none | 0.12 | 0 | 0
Zone 1- Shipping, North Mole Road, GibMaroc | 2018-03-07 | DM23-1 |  | 0.009 | clear | 210 | 755 | none | 8.17 | none | 0.14 | 0 | 0
Zone2-Low Level - Gibraltar College | 2018-03-07 | DM23-2 |  | 0.014 | clear | 202 | 740 | none | 8.28 | none | 0.18 | 0 | 0
Zone 3-Europa District- Europa Point toilets | 2018-03-07 | DM23-3 |  | 0.009 | clear | 211 | 761 | none | 8.2 | none | 0.16 | 0 | 0
Zone 4 - Upper Rock, Moorish Castle tourist site | 2018-03-07 | DM23-4 |  | <0.009 | clear | 200 | 776 | none | 8.29 | none | 0.1 | 0 | 0
Zone 1- Westside, Morrisons Superstore | 2018-03-13 | DM23-5 |  | <0.009 | clear | 170 | 759 | none | 8.05 | none | 0.21 | 0 | 0
Zone 2-Low Level - Bristol Hotel | 2018-03-13 | DM23-6 |  | <0.009 | clear | 235 | 795 | none | 7.97 | none | 0.09 | 0 | 0
Zone 3-Europa Distrct - Cliffton Mews | 2018-03-13 | DM23-7 |  | <0.009 | clear | 201 | 781 | none | 8.02 | none | 0.1 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2018-03-13 | DM23-8 |  | <0.009 | clear | 205 | 768 | none | 8.09 | none | 0.19 | 0 | 0
Zone 1-SD, New Mole House Central Police Station, Rosia Road | 2018-03-18 | DM23-9 |  | <0.009 | clear | 188 | 791 | none | 7.89 | none | 0.1 | 0 | 0
Zone 2-Low Level- Kings Bastion Leisure Centre | 2018-03-18 | DM23-10 |  | <0.009 | clear | 229 | 758 | none | 7.84 | none | 0.11 | 0 | 0
Zone 3-Europa District- Europa Point toilets | 2018-03-18 | DM23-11 |  | <0.009 | clear | 184 | 799 | none | 7.75 | none | 0.24 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2018-03-18 | DM23-12 |  | <0.009 | clear | 172 | 802 | none | 7.86 | none | 0.18 | 0 | 0
Zone 1- High Level, Arengo's nursery | 2018-03-27 | DM23-13 |  | <0.009 | clear | 209 | 741 | none | 7.78 | none | 0.24 | 0 | 0
Zone 2-Low Level- Gib Oil, Line Wall Road | 2018-03-27 | DM23-14 |  | <0.009 | clear | 223 | 756 | none | 7.86 | none | 0.1 | 0 | 0
Zone 3-Europa District - Eliotts Battery | 2018-03-27 | DM23-15 |  | <0.009 | clear | 212 | 761 | none | 7.93 | none | 0.19 | 0 | 0
Zone 4- Upper Rock, Devil's Gap | 2018-03-27 | DM23-16 |  | <0.009 | clear | 199 | 737 | none | 7.96 | none | 0.09 | 0 | 0
Zone 1- North Front, Beach View Terraces | 2018-04-03 | DA23-1 |  | <0.009 | clear | 182 | 664 | none | 7.92 | none | 0.11 | 0 | 0
Zone2-LL- Piazza | 2018-04-03 | DA23-2 |  | <0.009 | clear | 177 | 706 | none | 8.01 | none | 0.24 | 0 | 0
Zone 3-ED- Cliffton Mews | 2018-04-03 | DA23-3 |  | <0.009 | clear | 198 | 634 | none | 7.92 | none | 0.12 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2018-04-03 | DA23-4 |  | <0.009 | clear | 186 | 645 | none | 8.03 | none | 0.15 | 0 | 0
Zone 1- Moorish Castle Estate, 1 Castle House | 2018-04-10 | DA23-5 |  | <0.009 | clear | 182 | 663 | none | 8.18 | none | 0.1 | 0 | 0
Zone 2-LL - 39 Town Range, Senior Citizens Social Club | 2018-04-10 | DA23-6 |  | <0.009 | clear | 203 | 668 | none | 8.08 | none | 0.12 | 0 | 0
Zone 3-ED- Europa Point toilets | 2018-04-10 | DA23-7 |  | <0.009 | clear | 168 | 640 | none | 8.05 | none | 0.2 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2018-04-10 | DA23-8 |  | <0.009 | clear | 170 | 642 | none | 8.13 | none | 0.09 | 0 | 0
Zone 1- Shipping, AquaGib, M&E Depot | 2018-04-16 | DA23-9 |  | <0.009 | clear | 193 | 691 | none | 8.17 | none | 0.12 | 0 | 0
Zone 2-LL- Rock on the Rock Club, 41 Town Range | 2018-04-16 | DA23-10 |  | <0.009 | clear | 196 | 700 | none | 8.21 | none | 0.13 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-04-16 | DA23-11 |  | <0.009 | clear | 187 | 687 | none | 8.13 | none | 0.17 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2018-04-16 | DA23-12 |  | <0.009 | clear | 173 | 690 | none | 8.16 | none | 0.24 | 0 | 0
Zone 1- Westside, Westview Park playground toilet | 2018-04-27 | DA23-13 |  | <0.009 | clear | 194 | 720 | none | 8.03 | none | 0.11 | 0 | 0
Zone 2-LL- Gibraltar College | 2018-04-27 | DA23-14 |  | <0.009 | clear | 192 | 706 | none | 8.15 | none | 0.18 | 0 | 0
Zone 3-ED- Elliotts Battery, garden hose tap | 2018-04-27 | DA23-15 |  | <0.009 | clear | 164 | 603 | none | 8.14 | none | 0.08 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-04-27 | DA23-16 |  | <0.009 | clear | 186 | 693 | none | 8.13 | none | 0.09 | 0 | 0
Zone 1- South District, City Fire Brigade | 2018-05-02 | DM24-1 |  | <0.009 | clear | 174 | 675 | none | 8.25 | none | 0.11 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2018-05-02 | DM24-2 |  | <0.009 | clear | 184 | 704 | none | 8.12 | none | 0.17 | 0 | 0
Zone 3-ED- Cliffton Mews | 2018-05-02 | DM24-3 |  | <0.009 | clear | 164 | 681 | none | 8.25 | none | 0.09 | 0 | 0
Zone 4 - Upper Rock, Moorish Castle tourist site | 2018-05-02 | DM24-4 |  | <0.009 | clear | 178 | 692 | none | 8.15 | none | 0.08 | 0 | 0
Zone 1- Westside, Morrisons | 2018-05-10 | DM24-5 |  | <0.009 | clear | 237 | 850 | none | 8.15 | none | 0.09 | 0 | 0
Zone 2-LL - 39 Town Range, Senior Citizens Social Club | 2018-05-10 | DM24-6 |  | <0.009 | clear | 207 | 748 | none | 8.18 | none | 0.09 | 0 | 0
Zone 3-ED- Europa Point toilets | 2001-05-10 | DM24-7 |  | <0.009 | clear | 237 | 867 | none | 8.19 | none | 0.09 | 0 | 0
Zone 4- Upper rock, Lower Bruce's Farm | 2018-05-10 | DM24-8 |  | <0.009 | clear | 207 | 750 | none | 8.22 | none | 0.08 | 0 | 0
Zone 1- High Level, 50 Town Range, Leanse Place, AquaGib | 2018-05-16 | DM24-9 |  | <0.009 | clear | 209 | 792 | none | 8.11 | none | 0.19 | 0 | 0
Zone 2-LL- Gibraltar Chronicle | 2018-05-16 | DM24-10 |  | <0.009 | clear | 213 | 739 | none | 8.12 | none | 0.18 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-05-17 | DM24-11 |  | <0.009 | clear | 192 | 729 | none | 8.21 | none | 0.1 | 0 | 0
Zone 4- Upper rock, Upper Galleries (site office) | 2018-05-16 | DM24-12 |  | <0.009 | clear | 199 | 775 | none | 8.17 | none | 0.29 | 0 | 0
Zone 1- Moorish Castle Estate | 2018-05-23 | DM24-13 |  | <0.009 | clear | 203 | 712 | none | 8.27 | none | 0.09 | 0 | 0
Zone 2-LL- Gibraltar College | 2018-05-23 | DM24-14 |  | <0.009 | clear | 213 | 734 | none | 8.21 | none | 0.17 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-05-23 | DM24-15 |  | <0.009 | clear | 198 | 721 | none | 8.25 | none | 0.22 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-05-23 | DM24-16 |  | <0.009 | clear | 196 | 724 | none | 8.17 | none | 0.11 | 0 | 0
Zone 1- Shipping, AquaGib, Distiller depot | 2018-05-30 | DM24-13 |  | <0.009 | clear | 223 | 704 | none | 8.32 | none | 0.1 | 0 | 0
Zone 2-LL- Piazza, public toilets | 2018-05-30 | DM24-14 |  | <0.009 | clear | 189 | 723 | none | 8.28 | none | 0.2 | 0 | 0
Zone 3-ED- Eliotts Battery | 2018-05-30 | DM24-15 |  | <0.009 | clear | 175 | 710 | none | 8.26 | none | 0.23 | 0 | 0
Zone 4- Upper Rock, Poca Rocca | 2018-05-30 | DM24-16 |  | <0.009 | clear | 203 | 706 | none | 8.31 | none | 0.22 | 0 | 0
Zone 1- North Front, Eastern Beach, Motor vehicle test centre | 2018-06-04 | DJ35-1 |  | <0.009 | clear | 178 | 699 | none | 8.28 | none | 0.08 | 0 | 0
Zone2-LL- 8-10 Cathedral Square, Bristol Hotel | 2018-06-04 | DJ35-2 |  | <0.009 | clear | 209 | 725 | none | 8.24 | none | 0.3 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-06-04 | DJ35-3 |  | <0.009 | clear | 171 | 672 | none | 8.2 | none | 0.11 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2018-06-04 | DJ35-4 |  | <0.009 | clear | 203 | 706 | none | 8.28 | none | 0.19 | 0 | 0
Zone 1- S/D, AquaGib, Ragged staff depot, mess room kitchen | 2018-06-12 | DJ35-5 |  | <0.009 | clear | 166 | 692 | none | 8.39 | none | 0.1 | 0 | 0
Zone 2-LL - Cheers, Cornwalls Parade | 2018-06-14 | DJ35-6 |  | <0.009 | clear | 218 | 710 | none | 8.21 | none | 0.11 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-06-14 | DJ35-7 |  | <0.009 | clear | 186 | 677 | none | 8.17 | none | 0.19 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2018-06-14 | DJ35-8 |  | <0.009 | clear | 200 | 866 | none | 8.37 | none | 0.1 | 0 | 0
Zone 1- Westside District, Timeout Café | 2018-06-19 | DJ35-9 |  | <0.009 | clear | 232 | 750 | none | 8.15 | none | 0.23 | 0 | 0
Zone 2-LL- ICC toilets | 2018-06-19 | DJ35-10 |  | <0.009 | clear | 211 | 768 | none | 8.27 | none | 0.12 | 0 | 0
Zone 3-ED- Europa Point toilets | 2018-06-19 | DJ35-11 |  | <0.009 | clear | 200 | 717 | none | 8.35 | none | 0.08 | 0 | 0
Zone 4- Upper rock, Hayes Level, WWII Tunnels tourist site | 2018-06-19 | DJ35-12 |  | <0.009 | clear | 213 | 746 | none | 8.37 | none | 0.17 | 0 | 0
Zone 1- Moorish Castle Estate, 2 Castle House | 2018-07-02 | DJ36-1 |  | <0.009 | clear | 181 | 687 | none | 8.31 | none | 0.11 | 0 | 0
Zone2-LL- Gibraltar Regiment Social Club | 2018-07-04 | DJ36-2 |  | <0.009 | clear | 181 | 756 | none | 8.21 | none | 0.09 | 0 | 0
Zone 3-ED- Europa Point Toilets | 2018-07-04 | DJ36-3 |  | <0.009 | clear | 153 | 716 | none | 8.31 | none | 0.1 | 0 | 0
Zone 4 - Upper Rock, Moorish Castle Tourist Site | 2018-07-02 | DJ36-4 |  | <0.009 | clear | 159 | 722 | none | 8.34 | none | 0.08 | 0 | 0
Zone 1- S/D, Shipping district, GibFibrespeed, Waterport Rd | 2018-07-09 | DJ36-5 |  | <0.009 | clear | 170 | 677 | none | 8.28 | none | 0.09 | 0 | 0
Zone 2-LL - Gibraltar College | 2018-07-11 | DJ36-6 |  | <0.009 | clear | 203 | 740 | none | 8.36 | none | 0.13 | 0 | 0
Zone 3-ED- Higcliffe House | 2018-07-11 | DJ36-7 |  | <0.009 | clear | 179 | 703 | none | 84 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2018-07-09 | DJ36-8 |  | <0.009 | clear | 186 | 689 | none | 8.38 | none | 0.07 | 0 | 0
Zone 1- North Front, Eastern beach toilets | 2018-07-16 | DJ36-9 |  | <0.009 | clear | 178 | 731 | none | 8.36 | none | 0.09 | 0 | 0
Zone 2-LL- Engineers Lane | 2018-07-16 | DJ36-10 |  | <0.009 | clear | 197 | 731 | none | 8.34 | none | 0.42 | 0 | 0
Zone 3-ED- Eliotts Battery | 2018-07-19 | DJ36-11 |  | <0.009 | clear | 180 | 651 | none | 8.32 | none | 0.13 | 0 | 0
Zone 4- Upper Rock, Poca Rocca | 2018-07-19 | DJ36-12 |  | <0.009 | clear | 200 | 710 | none | 8.34 | none | 0.13 | 0 | 0
Zone 1- South District | 2018-07-23 | DJ36-13 |  | <0.009 | clear | 194 | 636 | none | 8.27 | none | 0.08 | 0 | 0
Zone 2-LL- Gibraltar Chronicle | 2018-07-26 | DJ36-14 |  | <0.009 | clear | 168 | 705 | none | 8.26 | none | 0.19 | 0 | 0
Zone 3-ED- Clifftons | 2018-07-23 | DJ36-15 |  | <0.009 | clear | 182 | 638 | none | 8.28 | none | 0.15 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-07-26 | DJ36-16 |  | <0.009 | clear | 171 | 691 | none | 8.39 | none | 0.08 | 0 | 0
Zone 1- Shipping, AquaGib, Distiller depot | 2018-08-01 | DA24-1 |  | <0.009 | clear | 188 | 674 | none | 8.79 | none | 0.13 | 0 | 0
Zone 2-LL- John Macintosh Hall | 2018-08-02 | DA24-2 |  | <0.009 | clear | 152 | 684 | none | 8.23 | none | 0.16 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-08-01 | DA24-3 |  | <0.009 | clear | 154 | 633 | none | 8.31 | none | 0.07 | 0 | 0
Zone 4- Upper Rock, WWII Tunnels | 2018-08-02 | DA24-4 |  | <0.009 | clear | 171 | 620 | none | 8.26 | none | 0.08 | 0 | 0
Zone 1 - North Front, Eastern Beach Toilets | 2018-08-08 | DA24-5 |  | <0.009 | clear | 190 | 738 | none | 8.36 | none | 0.11 | 0 | 0
Zone 2-LL - Piazza | 2018-08-06 | DA24-6 |  | <0.009 | clear | 180 | 680 | none | 8.24 | none | 0.15 | 0 | 0
Zone 3-ED- Elliotts Battery | 2018-08-06 | DA24-7 |  | <0.009 | clear | 153 | 767 | none | 8.36 | none | 0.08 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2018-08-08 | DA24-8 |  | <0.009 | clear | 192 | 784 | none | 8.42 | none | 0.07 | 0 | 0
Zone 1- Westside, GASA | 2018-08-15 | DA24-9 |  | <0.009 | clear | 179 | 685 | none | 8.01 | none | 0.11 | 0 | 0
Zone 2-LL- Kings Bastion Leisure Centre | 2018-08-15 | DA24-10 |  | <0.009 | clear | 203 | 659 | none | 8.22 | none | 0.12 | 0 | 0
Zone 3-ED- Europa point toilets | 2018-08-15 | DA24-11 |  | <0.009 | clear | 167 | 712 | none | 8.32 | none | 0.14 | 0 | 0
Zone 4- Upper Rock, MC tourist site | 2018-08-15 | DA24-12 |  | <0.009 | clear | 156 | 642 | none | 8.25 | none | 0.08 | 0 | 0
Zone 1- High Level | 2018-08-22 | DA24-13 |  | <0.009 | clear | 171 | 738 | none | 8.3 | none | 0.12 | 0 | 0
Zone 2-LL- Gib Regiment Social Club | 2018-08-20 | DA24-14 |  | <0.009 | clear | 189 | 721 | none | 8.31 | none | 0.13 | 0 | 0
Zone 3-ED- Clifftons | 2018-08-22 | DA24-15 |  | <0.009 | clear | 188 | 799 | none | 8.4 | none | 0.09 | 0 | 0
Zone 4- Upper Rock, Devil's Gap | 2018-08-22 | DA24-16 |  | <0.009 | clear | 192 | 796 | none | 8.39 | none | 0.12 | 0 | 0
Zone 1- Moorish Castle Estate | 2018-08-28 | DA24-17 |  | <0.009 | clear | 198 | 824 | none | 8.21 | none | 0.09 | 0 | 0
Zone 2-LL- John Macintosh Hall | 2018-08-28 | DA24-18 |  | <0.009 | clear | 163 | 743 | none | 8.18 | none | 0.17 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-08-30 | DA24-19 |  | <0.009 | clear | 190 | 790 | none | 8.37 | none | 0.13 | 0 | 0
Zone 4- Upper Rock, Poca Rocca | 2018-08-28 | DA24-20 |  | <0.009 | clear | 169 | 796 | none | 8.34 | none | 0.08 | 0 | 0
Zone 1- South District, New Harbours, Coviran | 2018-09-05 | DS12-1 |  | <0.009 | clear | 215 | 813 | none | 8.24 | none | 0.19 | 0 | 0
Zone 2-LL- Gibraltar College | 2018-09-05 | DS12-2 |  | <0.009 | clear | 204 | 770 | none | 8.14 | none | 0.21 | 0 | 0
Zone 3-ED- Europa Point toilets | 2018-09-05 | DS12-3 |  | <0.009 | clear | 219 | 837 | none | 8.26 | none | 0.12 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-09-05 | DS12-4 |  | <0.009 | clear | 220 | 821 | none | 8.26 | none | 0.1 | 0 | 0
Zone 1 - North Front, Mauis Restaurant | 2018-09-11 | DS12-5 |  | <0.009 | clear | 227 | 784 | none | 8.24 | none | 0.11 | 0 | 0
Zone 2-LL - 5 Cornwalls Parade, Chandan Mini-supermarket | 2018-09-11 | DS12-6 |  | <0.009 | clear | 216 | 779 | none | 8.23 | none | 0.21 | 0 | 0
Zone 3-ED- Clifftons | 2018-09-11 | DS12-7 |  | <0.009 | clear | 223 | 791 | none | 8.28 | none | 0.19 | 0 | 0
Zone 4- Upper rock, WWII Tunnels tourist site | 2018-09-11 | DS12-8 |  | <0.009 | clear | 210 | 798 | none | 8.24 | none | 0.22 | 0 | 0
Zone 1- Westside, St Bernard's Hospital | 2018-09-17 | DS12-9 |  | <0.009 | clear | 223 | 754 | none | 8.25 | none | 0.17 | 0 | 0
Zone 2-LL- Gibraltar Chronicle | 2018-09-17 | DS12-10 |  | <0.009 | clear | 209 | 741 | none | 8.29 | none | 0.15 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-09-17 | DS12-11 |  | <0.009 | clear | 210 | 745 | none | 8.29 | none | 0.19 | 0 | 0
Zone 4- Upper Rock, Bruces Farm | 2018-09-17 | DS12-12 |  | <0.009 | clear | 218 | 753 | none | 8.34 | none | 0.24 | 0 | 0
Zone 1- High Level, Leanse Place, AquaGib Main Office | 2018-09-25 | DS12-13 |  | <0.009 | clear | 202 | 751 | none | 8.27 | none | 0.1 | 0 | 0
Zone 2-LL- Piazza public toilets | 2018-09-25 | DS12-14 |  | <0.009 | clear | 216 | 721 | none | 8.29 | none | 0.26 | 0 | 0
Zone 3-ED- Europa Point public toilets | 2018-09-25 | DS12-15 |  | <0.009 | clear | 180 | 630 | none | 8.44 | none | 0.16 | 0 | 0
Zone 4- Upper Rock, Moorish Castle tourist site | 2018-09-25 | DS12-16 |  | <0.009 | clear | 223 | 730 | none | 8.32 | none | 0.27 | 0 | 0
Zone 1- Moorish Castle Estate, 2 Castle House | 2018-10-02 | DO12-1 |  | <0.009 | clear | 220 | 728 | none | 7.99 | none | 0.08 | 0 | 0
Zone 2-LL- ICC toilets | 2018-10-02 | DO12-2 |  | <0.009 | clear | 195 | 747 | none | 8.12 | none | 0.1 | 0 | 0
Zone 3-ED- Cliffton Mews | 2018-10-02 | DO12-3 |  | <0.009 | clear | 226 | 677 | none | 7.45 | none | 0.19 | 0 | 0
Zone 4- Upper Rock, Great Siege Tunnels | 2018-10-02 | DO12-4 |  | <0.009 | clear | 227 | 690 | none | 7.16 | none | 0.12 | 0 | 0
Zone 1 - South District, Piccadily restaurant | 2018-10-11 | DO12-5 |  | <0.009 | clear | 223 | 796 | none | 8.42 | none | 0.21 | 0 | 0
Zone 2-LL - Queensway, Manchester Club | 2018-10-11 | DO12-6 |  | <0.009 | clear | 227 | 811 | none | 8.4 | none | 0.12 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-10-11 | DO12-7 |  | <0.009 | clear | 245 | 1080 | none | 8.41 | none | 0.1 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2018-10-11 | DO12-8 |  | <0.009 | clear | 207 | 774 | none | 8.44 | none | 0.12 | 0 | 0
Zone 1- North Front, Halifax Road, Gaggero Cemats | 2018-10-15 | DO12-9 |  | <0.009 | clear | 184 | 811 | none | 8.44 | none | 0.24 | 0 | 0
Zone 2-LL- Kings Bastion Leisure Centre | 2018-10-15 | DO12-10 |  | <0.009 | clear | 210 | 767 | none | 8.35 | none | 0.21 | 0 | 0
Zone 3-ED- Eliotts Battery | 2018-10-17 | DO12-11 |  | <0.009 | clear | 200 | 794 | none | 8.41 | none | 0.14 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-10-17 | DO12-12 |  | <0.009 | clear | 214 | 776 | none | 8.32 | none | 0.09 | 0 | 0
Zone 1- Westside, Europort roundabout, Mcdonalds | 2018-10-22 | DO12-13 |  | 0.01 | clear | 182 | 795 | none | 8.06 | none | 0.12 | 0 | 0
Zone 2-LL- Piazza public toilets | 2018-10-22 | DO12-14 |  | <0.009 | clear | 229 | 760 | none | 8.16 | none | 0.22 | 0 | 0
Zone 3-ED- Clifftons | 2018-10-22 | DO12-15 |  | <0.009 | clear | 184 | 796 | none | 8.27 | none | 0.09 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2018-10-22 | DO12-16 |  | <0.009 | clear | 213 | 786 | none | 8.16 | none | 0.12 | 0 | 0
Zone 1- High Level, Town Range, Senior Citizens club | 2018-10-31 | DO12-17 |  | <0.009 | clear | 196 | 740 | none | 8.37 | none | 0.18 | 0 | 0
Zone 2-LL- Watergate Hse, Casemates Sq, Gibraltar Chronicle | 2018-10-31 | DO12-18 |  | <0.009 | clear | 200 | 738 | none | 8.4 | none | 0.09 | 0 | 0
Zone 3-ED- Europa Point toilets | 2018-10-31 | DO12-19 |  | <0.009 | clear | 195 | 739 | none | 8.39 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Moorish Castle tourist site | 2018-10-31 | DO12-20 |  | <0.009 | clear | 201 | 764 | none | 8.34 | none | 0.15 | 0 | 0
Zone 1- Moorish Castle Estate, 2 Keightley House | 2018-11-06 | DN12-1 |  | <0.009 | clear | 174 | 708 | none | 8.34 | none | 0.15 | 0 | 0
Zone 2-LL- Piazza | 2018-11-06 | DN12-2 |  | <0.009 | clear | 196 | 751 | none | 8.19 | none | 0.2 | 0 | 0
Zone 3-ED- Cliffton Mews | 2018-11-06 | DN12-3 |  | <0.009 | clear | 177 | 717 | none | 8.37 | none | 0.19 | 0 | 0
Zone 4- Upper Rock, Devil's Gap | 2018-11-06 | DN12-4 |  | <0.009 | clear | 163 | 702 | none | 8.28 | none | 0.11 | 0 | 0
Zone 1 - South District, Vineyards | 2018-11-12 | DN12-5 |  | <0.009 | clear | 190 | 769 | none | 8.39 | none | 0.11 | 0 | 0
Zone 2-LL - Line Wall Road, Gib Oil | 2018-11-12 | DN12-6 |  | <0.009 | clear | 187 | 756 | none | 8.04 | none | 0.09 | 0 | 0
Zone 3-ED- Eliotts Battery | 2018-11-12 | DN12-7 |  | <0.009 | clear | 191 | 782 | none | 8.34 | none | 0.24 | 0 | 0
Zone 4- Upper Rock, Bruces Farm | 2018-11-12 | DN12-8 |  | <0.009 | clear | 185 | 772 | none | 8.31 | none | 0.15 | 0 | 0
Zone 1 - North Front, MOT test centre, Eastern Beach | 2018-11-20 | DN12-9 |  | 0.011 | clear | 194 | 731 | none | 8.33 | none | 0.2 | 0 | 0
Zone 2-LL - Midtown carpark | 2018-11-20 | DN12-10 |  | 0.01 | clear | 188 | 740 | none | 8.27 | none | 0.22 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-11-20 | DN12-11 |  | <0.009 | clear | 197 | 734 | none | 8.32 | none | 0.1 | 0 | 0
Zone 4- WWII Tunnels | 2018-11-20 | DN12-12 |  | 0.011 | clear | 190 | 749 | none | 8.26 | none | 0.14 | 0 | 0
Zone 1 - Westside, Europort Road, GASA swimming pool | 2018-11-26 | DN12-13 |  | <0.009 | clear | 187 | 725 | none | 8.45 | none | 0.1 | 0 | 0
Zone 2-LL - ICC toilets | 2018-11-26 | DN12-14 |  | <0.009 | clear | 187 | 721 | none | 8.32 | none | 0.28 | 0 | 0
Zone 3-ED- Eliotts Battery | 2018-11-26 | DN12-15 |  | <0.009 | clear | 198 | 748 | none | 8.3 | none | 0.16 | 0 | 0
Zone 4- Upper Rock, Upper Galleries | 2018-11-26 | DN12-16 |  | <0.009 | clear | 190 | 728 | none | 8.35 | none | 0.08 | 0 | 0
Zone 1- High Level, Willi's Road, Little Learners Nursery | 2018-12-06 | DD12-1 |  | <0.009 | clear | 180 | 781 | none | 8.29 | none | 0.22 | 0 | 0
Zone 2-LL- John Mackintosh Hall | 2018-12-06 | DD12-2 |  | <0.009 | clear | 209 | 736 | none | 8.36 | none | 0.19 | 0 | 0
Zone 3-ED- Cliffton Mews | 2018-12-06 | DD12-3 |  | <0.009 | clear | 223 | 872 | none | 8.31 | none | 0.09 | 0 | 0
Zone 4- Upper Rock, Poca Rocca | 2018-12-06 | DD12-4 |  | <0.009 | clear | 188 | 738 | none | 8.41 | none | 0.16 | 0 | 0
Zone 1 - Moorish Castle Estate, 10 MacMillan House | 2018-12-10 | DD12-5 |  | <0.009 | clear | 192 | 754 | none | 8.39 | none | 0.22 | 0 | 0
Zone 2-LL - Kings Bastion Leisure Centre | 2018-12-10 | DD12-6 |  | <0.009 | clear | 186 | 735 | none | 8.49 | none | 0.1 | 0 | 0
Zone 3-ED- Highcliffe House | 2018-12-10 | DD12-7 |  | <0.009 | clear | 185 | 744 | none | 8.37 | none | 0.16 | 0 | 0
Zone 4- Moorish Castle tourist site | 2018-12-10 | DD12-8 |  | <0.009 | clear | 201 | 739 | none | 8.32 | none | 0.14 | 0 | 0
Zone 1 - Shipping, Wastage, Waterport Terraces | 2018-12-17 | DD12-9 |  | <0.009 | clear | 184 | 739 | none | 8.28 | none | 0.1 | 0 | 0
Zone 2-LL - Department of Education, 23 Queensway | 2018-12-17 | DD12-10 |  | <0.009 | clear | 195 | 741 | none | 8.13 | none | 0.24 | 0 | 0
Zone 3-ED- Europa point toilets | 2018-12-17 | DD12-11 |  | <0.009 | clear | 190 | 744 | none | 8.18 | none | 0.15 | 0 | 0
Zone 4- Upper Rock, Devil's Gap | 2018-12-17 | DD12-12 |  | <0.009 | clear | 192 | 745 | none | 8.26 | none | 0.13 | 0 | 0
Zone1 - S Dist, New Harbours Industrial Estate, 101 Gibraltar | 2019-01-03 | DJ30-1 |  | <0.009 | clear | 189 | 771 | none | 8.33 | none | 0.14 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2019-01-03 | DJ30-2 |  | <0.009 | clear | 180 | 749 | none | 8.29 | none | 0.24 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-01-03 | DJ30-3 |  | <0.009 | clear | 211 | 792 | none | 8.25 | none | 0.08 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2019-01-03 | DJ30-4 |  | <0.009 | clear | 200 | 783 | none | 8.34 | none | 0.15 | 0 | 0
Zone 1- North Front, Beach View Terraces | 2019-01-10 | DJ30-5 |  | <0.009 | clear | 206 | 709 | none | 8.48 | none | 0.11 | 0 | 0
Zone 2-LL - Casemates | 2019-01-10 | DJ30-6 |  | <0.009 | clear | 183 | 718 | none | 8.34 | none | 0.13 | 0 | 0
Zone 3-ED- Clifftons | 2019-01-10 | DJ30-7 |  | <0.009 | clear | 179 | 712 | none | 8.48 | none | 0.19 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2019-01-10 | DJ30-8 |  | <0.009 | clear | 186 | 739 | none | 8.44 | none | 0.09 | 0 | 0
Zone 1- High Level, 32 Prince Edwards Road, Carters | 2019-01-14 | DJ30-9 |  | <0.009 | clear | 165 | 674 | none | 8.37 | none | 0.22 | 0 | 0
Zone 2-LL - Piazza | 2019-01-16 | DJ30-10 |  | 0.011 | clear | 201 | 727 | none | 8.41 | none | 0.11 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-01-14 | DJ30-11 |  | <0.009 | clear | 151 | 632 | none | 8.48 | none | 0.09 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-01-16 | DJ30-12 |  | 0.01 | clear | 190 | 693 | none | 8.33 | none | 0.09 | 0 | 0
Zone 1- Westside, Eurotowers, Timeout Café | 2019-01-21 | DJ30-13 |  | <0.009 | clear | 214 | 751 | none | 8.37 | none | 0.11 | 0 | 0
Zone 2-LL - King's Bastion Leisure Centre, 55 Line Wall Road | 2019-01-21 | DJ30-14 |  | <0.009 | clear | 189 | 731 | none | 8.31 | none | 0.21 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-01-21 | DJ30-15 |  | <0.009 | clear | 178 | 725 | none | 8.18 | none | 0.19 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-01-23 | DJ30-16 |  | <0.009 | clear | 192 | 751 | none | 8.4 | none | 0.13 | 0 | 0
Zone 1- High Level, Flat Bastion Road | 2019-01-28 | DJ30-17 |  | <0.009 | clear | 198 | 767 | none | 8.27 | none | 0.26 | 0 | 0
Zone 2-LL - John Mackintosh Hall | 2019-01-28 | DJ30-18 |  | <0.009 | clear | 211 | 735 | none | 8.29 | none | 0.11 | 0 | 0
Zone 3-ED- Block 23, Eliotts Battery | 2019-01-28 | DJ30-19 |  | <0.009 | clear | 219 | 776 | none | 8.34 | none | 0.16 | 0 | 0
Zone 4- Upper rock, Moorish Castle tourist site | 2019-01-30 | DJ30-20 |  | <0.009 | clear | 173 | 782 | none | 8.44 | none | 0.19 | 0 | 0
Zone1 - Shipping, Waterport, Care Agency | 2019-02-05 | DF10-1 |  | <0.009 | clear | 171 | 752 | none | 8.4 | none | 0.18 | 0 | 0
Zone2-LL- Piazza | 2019-02-08 | DF10-2 |  | <0.009 | clear | 182 | 757 | none | 7.9 | none | 0.24 | 0 | 0
Zone 3-ED- The Clifftons | 2019-02-08 | DF10-3 |  | <0.009 | clear | 176 | 765 | none | 8.32 | none | 0.19 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2019-02-08 | DF10-4 |  | <0.009 | clear | 192 | 771 | none | 8.27 | none | 0.14 | 0 | 0
Zone 1- Moorish Castle Estate, 8 Key House | 2019-02-11 | DF10-5 |  | <0.009 | clear | 198 | 771 | none | 8.32 | none | 0.12 | 0 | 0
Zone 2-LL - Midtown coach park | 2019-02-11 | DF10-6 |  | <0.009 | clear | 195 | 763 | none | 8.3 | none | 0.16 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-02-11 | DF10-7 |  | <0.009 | clear | 217 | 793 | none | 8.39 | none | 0.1 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-02-11 | DF10-8 |  | <0.009 | clear | 210 | 796 | none | 8.24 | none | 0.19 | 0 | 0
Zone 1- South District, New Harbours, Coviran | 2019-02-20 | DF10-9 |  | <0.009 | clear | 175 | 692 | none | 8.44 | none | 0.16 | 0 | 0
Zone 2-LL-122 Irish Town, Royal Gibraltar Regiment Association | 2019-02-20 | DF10-10 |  | <0.009 | clear | 209 | 745 | none | 8.36 | none | 0.21 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-02-20 | DF10-11 |  | <0.009 | clear | 162 | 668 | none | 8.5 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-02-20 | DF10-12 |  | <0.009 | clear | 206 | 760 | none | 8.36 | none | 0.19 | 0 | 0
Zone 1- North Front, MOT Centre | 2019-02-27 | DF10-13 |  | <0.009 | clear | 199 | 726 | none | X | none | 0.14 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2019-02-27 | DF10-14 |  | <0.009 | clear | 213 | 731 | none | X | none | 0.21 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-02-27 | DF10-15 |  | <0.009 | clear | 206 | 746 | none | X | none | 0.11 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-02-27 | DF10-16 |  | <0.009 | clear | 192 | 747 | none | X | none | 0.2 | 0 | 0
Zone1 - Westside, 3 Waterport Road, Pig & Whistle | 2019-03-07 | DM20-1 |  | <0.009 | clear | 201 | 743 | none | 8.26 | none | 0.1 | 0 | 0
Zone2-LL- Gibraltar College , Line Wall Road | 2019-03-07 | DM20-2 |  | <0.009 | clear | 198 | 745 | none | 8.25 | none | 0.13 | 0 | 0
Zone 3-ED- Clifftons | 2019-03-07 | DM20-3 |  | <0.009 | clear | 221 | 761 | none | 8.32 | none | 0.18 | 0 | 0
Zone 4 - Upper Rock, WWII Tunnels | 2019-03-07 | DM20-4 |  | <0.009 | clear | 198 | 733 | none | 8.27 | none | 0.26 | 0 | 0
Zone 1- NF, High Level, 57 Willis' Road, Little Learner's Nursery | 2019-03-12 | DM20-5 |  | <0.009 | clear | 191 | 722 | none | 8.48 | none | 0.23 | 0 | 0
Zone 2-LL - ICC Toilets | 2019-03-14 | DM20-6 |  | <0.009 | clear | 183 | 707 | none | 8.33 | none | 0.11 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-03-14 | DM20-7 |  | <0.009 | clear | 178 | 681 | none | 8.41 | none | 0.09 | 0 | 0
Zone 4- Upper rock, Bruce's Farm | 2019-03-14 | DM20-8 |  | <0.009 | clear | 197 | 733 | none | 8.46 | none | 0.15 | 0 | 0
Zone 1- Shipping, Flying Angel | 2019-03-18 | DM20-9 |  | <0.009 | clear | 222 | 731 | none | 8.4 | none | 0.19 | 0 | 0
Zone 2-LL - Casemates square toilet | 2019-03-18 | DM20-10 |  | <0.009 | clear | 159 | 720 | none | 8.46 | none | 0.14 | 0 | 0
Zone 3-ED- Brympton, 7A Victoria Residency | 2019-03-20 | DM20-11 |  | <0.009 | clear | 217 | 783 | none | 8.48 | none | 0.14 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-03-20 | DM20-12 |  | <0.009 | clear | 210 | 785 | none | 8.5 | none | 0.22 | 0 | 0
Zone1 - Moorish Castle Estate, Oli's Takeaway | 2019-03-25 | DM20-13 |  | <0.009 | clear | 223 | 754 | none | 8.42 | none | 0.17 | 0 | 0
Zone 2-LL - King's Bastion Leisure Centre, 55 Line Wall Road | 2019-03-25 | DM20-14 |  | <0.009 | clear | 212 | 744 | none | 8.43 | none | 0.1 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-03-27 | DM20-15 |  | <0.009 | clear | 211 | 729 | none | 8.42 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-03-27 | DM20-16 |  | <0.009 | clear | 203 | 735 | none | 8.39 | none | 0.09 | 0 | 0
Zone1-South Dist, New Harbours Industrial Estate, 101 Gibraltar | 2019-04-03 | DA20-1 |  | <0.009 | clear | 230 | 735 | none | 8.27 | none | 0.12 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2019-04-03 | DA20-2 |  | <0.009 | clear | 220 | 731 | none | 8.31 | none | 0.14 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-04-03 | DA20-3 |  | <0.009 | clear | 217 | 737 | none | 8.23 | none | 0.19 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2019-04-03 | DA20-4 |  | <0.009 | clear | 209 | 729 | none | 8.3 | none | 0.18 | 0 | 0
Zone 1- North Front, Bayside Road, Tercentenary Sports Hall | 2019-04-08 | DA20-5 |  | <0.009 | clear | 171 | 688 | none | 8.28 | none | 0.12 | 0 | 0
Zone 2-LL - Gibraltar College, South Bastion, Line Wall Road | 2019-04-08 | DA20-6 |  | <0.009 | clear | 189 | 713 | none | 8.23 | none | 0.2 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-04-08 | DA20-7 |  | <0.009 | clear | 186 | 659 | none | 8.27 | none | 0.15 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2019-04-08 | DA20-8 |  | <0.009 | clear | 196 | 698 | none | 8.29 | none | 0.17 | 0 | 0
Zone 1- Westsid, GASA swimming pool | 2019-04-15 | DA20-9 |  | <0.009 | clear | 186 | 701 | none | 8.36 | none | 0.16 | 0 | 0
Zone 2-LL - Chatham Counterguard | 2019-04-15 | DA20-10 |  | <0.009 | clear | 189 | 727 | none | 8.42 | none | 0.13 | 0 | 0
Zone 3-ED- Highcliff House | 2019-04-15 | DA20-11 |  | <0.009 | clear | 179 | 679 | none | 8.45 | none | 0.21 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-04-15 | DA20-12 |  | <0.009 | clear | 204 | 701 | none | 8.48 | none | 0.15 | 0 | 0
Zone1-HL Leanse place head office Kitchen | 2019-04-26 | DA20-13 |  | <0.009 | clear | 167 | 676 | none | 8.1 | none | 0.36 | 0 | 0
Zone 2-LL - Giboil Line wall road | 2019-04-26 | DA20-14 |  | <0.009 | clear | 171 | 689 | none | 8.11 | none | 0.58 | 0 | 0
Zone 3-Lathbury ED Sacarellos | 2019-04-26 | DA20-15 |  | <0.009 | clear | 165 | 665 | none | 8.11 | none | 0.35 | 0 | 0
Zone 4- MH Upper Rock Bruce's farm | 2019-04-26 | DA20-16 |  | <0.009 | clear | 163 | 660 | none | 8.1 | none | 0.34 | 0 | 0
Zone1 - Shipping, Waterport Road, Wastage | 2019-05-04 | DM21-1 |  | <0.009 | clear | 185 | 601 | none | 7.95 | none | 0.07 | 0 | 0
Zone2-LL- Piazza | 2019-05-04 | DM21-2 |  | <0.009 | clear | 185 | 616 | none | 8.06 | none | 0.52 | 0 | 0
Zone 3-ED- Clifftons | 2019-05-04 | DM21-3 |  | <0.009 | clear | 181 | 606 | none | 8.09 | none | 0.14 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2019-04-30 | DM21-4 |  | 0.013 | clear | 179 | 680 | none | 8 | none | 0.67 | 0 | 0
Zone 1- Moorish Castle Estate, 10 MacMillan House | 2019-05-09 | DM21-5 |  | <0.009 | clear | 179 | 643 | none | 8.13 | none | X | 0 | 0
Zone 2-LL - 24 Wellington Front | 2019-05-09 | DM21-6 |  | <0.009 | clear | 179 | 645 | none | 8.21 | none | X | 0 | 0
Zone 3-ED- Sacarellos, Alectoris Lane | 2019-05-09 | DM21-7 |  | <0.009 | clear | 179 | 633 | none | 8.18 | none | X | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-05-09 | DM21-8 |  | <0.009 | clear | 173 | 638 | none | 8.15 | none | X | 0 | 0
Zone 1- South District, Heathfield House, Upper Witham's Road | 2019-05-16 | DM21-9 |  | <0.009 | clear | 169 | 677 | none | 8.19 | none | 0.12 | 0 | 0
Zone 2-LL - Kings Bastion Leisure Centre | 2019-05-16 | DM21-10 |  | <0.009 | clear | 172 | 653 | none | 8.24 | none | 0.24 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-05-16 | DM21-11 |  | <0.009 | clear | 163 | 664 | none | 8.28 | none | 0.16 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2019-05-16 | DM21-12 |  | <0.009 | clear | 159 | 624 | none | 8.11 | none | 0.1 | 0 | 0
Zone 1- North Front, Caleta Hotel | 2019-05-21 | DM21-13 |  | <0.009 | clear | 193 | 694 | none | 8.28 | none | 0.09 | 0 | 0
Zone 2-LL - ICC | 2019-05-21 | DM21-14 |  | <0.009 | clear | 199 | 679 | none | 8.24 | none | 0.18 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-05-21 | DM21-15 |  | <0.009 | clear | 178 | 683 | none | 8.26 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-05-21 | DM21-16 |  | <0.009 | clear | 196 | 688 | none | 8.25 | none | 0.19 | 0 | 0
Zone 1- Westside, GASA | 2019-05-28 | DM21-17 |  | <0.009 | clear | 201 | 678 | none | 8.17 | none | 0.19 | 0 | 0
Zone 2-LL - Casemates | 2019-05-28 | DM21-18 |  | <0.009 | clear | 180 | 674 | none | 8.2 | none | 0.13 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-05-28 | DM21-19 |  | <0.009 | clear | 173 | 683 | none | 8.22 | none | 0.1 | 0 | 0
Zone 4- Upper rock, Bruce's Farm | 2019-05-28 | DM21-20 |  | <0.009 | clear | 188 | 681 | none | 8.29 | none | 0.15 | 0 | 0
Zone1 - High Level, Town Range, Senior Citizens social club | 2019-06-03 | DJ31-1 |  | <0.009 | clear | 194 | 675 | none | 8.27 | none | 0.19 | 0 | 0
Zone2-LL- John Mackintosh Hall | 2019-06-03 | DJ31-2 |  | <0.009 | clear | 189 | 685 | none | 8.23 | none | 0.14 | 0 | 0
Zone 3-ED- Clifftons | 2019-06-03 | DJ31-3 |  | <0.009 | clear | 180 | 679 | none | 8.3 | none | 0.1 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2019-06-03 | DJ31-4 |  | <0.009 | clear | 179 | 682 | none | 8.29 | none | 0.08 | 0 | 0
Zone 1- Shipping, AquaGib, Distiller depot | 2019-06-10 | DJ31-5 |  | <0.009 | clear | 165 | 685 | none | 8.28 | none | 0.14 | 0 | 0
Zone 2-LL - Line Wall Road, Gib Oil | 2019-06-10 | DJ31-6 |  | <0.009 | clear | 196 | 674 | none | 8.2 | none | 0.16 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-06-10 | DJ31-7 |  | <0.009 | clear | 169 | 678 | none | 8.17 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-06-10 | DJ31-8 |  | <0.009 | clear | 192 | 695 | none | 8.29 | none | 0.12 | 0 | 0
Zone 1- High Level, 32 Prince Edwards Road, Carters | 2019-06-18 | DJ31-9 |  | <0.009 | clear | 198 | 732 | none | 8.23 | none | 0.19 | 0 | 0
Zone 2-LL - Piazza | 2019-06-18 | DJ31-10 |  | <0.009 | clear | 189 | 711 | none | 8.18 | none | 0.1 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-06-18 | DJ31-11 |  | <0.009 | clear | 193 | 724 | none | 8.26 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-06-18 | DJ31-12 |  | <0.009 | clear | 186 | 744 | none | 8.19 | none | 0.11 | 0 | 0
Zone 1- Moorish Castle Estate, Ollie's Takeaway | 2019-06-26 | DJ31-13 |  | <0.009 | clear | 179 | 693 | none | 8.3 | none | 0.09 | 0 | 0
Zone 2-LL - ICC toilets | 2019-06-26 | DJ31-14 |  | <0.009 | clear | 186 | 696 | none | 8.33 | none | 0.14 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-06-26 | DJ31-15 |  | <0.009 | clear | 195 | 718 | none | 8.36 | none | 0.27 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-06-26 | DJ31-16 |  | <0.009 | clear | 193 | 723 | none | 8.39 | none | 0.18 | 0 | 0
Zone1 - Westside, Tecentenary Sports Hall | 2019-07-03 | DJ32-1 |  | <0.009 | clear | 167 | 714 | none | 8.1 | none | 0.29 | 0 | 0
Zone2-LL- Piazza | 2019-07-03 | DJ32-2 |  | <0.009 | clear | 200 | 717 | none | 8.1 | none | 0.12 | 0 | 0
Zone 3-ED- Sacarellos | 2019-07-03 | DJ32-3 |  | <0.009 | clear | 210 | 728 | none | 8.22 | none | 0.22 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2019-07-03 | DJ32-4 |  | <0.009 | clear | 181 | 738 | none | 8.24 | none | 0.23 | 0 | 0
Zone 1- North Front, Eastern Beach toilet facilities | 2019-07-11 | DJ32-5 |  | <0.009 | clear | 160 | 714 | none | 8.05 | none | 0.15 | 0 | 0
Zone 2-LL - Gibraltar Chronicle | 2019-07-11 | DJ32-6 |  | <0.009 | clear | 174 | 709 | none | 8.09 | none | 0.24 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-07-11 | DJ32-7 |  | <0.009 | clear | 169 | 723 | none | 8.09 | none | 0.3 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-07-09 | DJ32-8 |  | <0.009 | clear | 163 | 711 | none | 8.17 | none | 0.23 | 0 | 0
Zone 1- High Level, AquaGib Office, Leanse Place | 2019-07-15 | DJ32-9 |  | <0.009 | clear | 155 | 707 | none | 8.04 | none | 0.31 | 0 | 0
Zone 2-LL - John Mackintosh Hall | 2019-07-17 | DJ32-10 |  | <0.009 | clear | 158 | 734 | none | 7.88 | none | 0.32 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-07-17 | DJ32-11 |  | <0.009 | clear | 155 | 782 | none | 8.11 | none | 0.35 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-07-17 | DJ32-12 |  | <0.009 | clear | 164 | 726 | none | 8.07 | none | 0.33 | 0 | 0
Zone 1- High Level, South District, Transport Lane | 2019-07-23 | DJ32-13 |  | <0.009 | clear | 170 | 749 | none | 8.14 | none | 0.15 | 0 | 0
Zone 2-LL - Line Wall Road, Gib Oil | 2019-07-23 | DJ32-14 |  | <0.009 | clear | 181 | 729 | none | 8.15 | none | 0.16 | 0 | 0
Zone 3-ED- The Mount | 2019-07-23 | DJ32-15 |  | <0.009 | clear | 189 | 757 | none | 8.23 | none | 0.19 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2019-07-23 | DJ32-16 |  | <0.009 | clear | 201 | 752 | none | 8.13 | none | 0.18 | 0 | 0
Zone1 - Shipping, Flying Angel | 2019-07-31 | DA21-1 |  | <0.009 | clear | 157 | 762 | none | 7.89 | none | 0.23 | 0 | 0
Zone2-LL- Gibraltar Regiment Social Club | 2019-07-31 | DA21-2 |  | <0.009 | clear | 158 | 731 | none | 8.03 | none | 0.19 | 0 | 0
Zone 3-ED- Clifftons | 2019-07-31 | DA21-3 |  | <0.009 | clear | 153 | 689 | none | 8.09 | none | 0.13 | 0 | 0
Zone 4 - Upper Rock, Devils Gap | 2019-07-31 | DA21-4 |  | <0.009 | clear | 164 | 708 | none | 8.02 | none | 0.2 | 0 | 0
Zone 1- Westside, GASA swimming pool | 2019-08-05 | DA21-5 |  | <0.009 | clear | 159 | 696 | none | 8.15 | none | 0.18 | 0 | 0
Zone 2-LL - John Mackintosh Hall | 2019-08-07 | DA21-6 |  | <0.009 | clear | 172 | 711 | none | 7.93 | none | 0.17 | 0 | 0
Zone 3-ED- Naval Hospital Hill | 2019-08-07 | DA21-7 |  | <0.009 | clear | 165 | 694 | none | 8.03 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2019-08-07 | DA21-8 |  | <0.009 | clear | 171 | 696 | none | 7.99 | none | 0.18 | 0 | 0
Zone 1- North Front, Eastern Beach Toilets | 2019-08-12 | DA21-9 |  | <0.009 | clear | 183 | 715 | none | 8.11 | none | 0.17 | 0 | 0
Zone 2-LL - Piazza | 2019-08-12 | DA21-10 |  | <0.009 | clear | 178 | 709 | none | 8.1 | none | 0.24 | 0 | 0
Zone 3-ED- Highcliffe house | 2019-08-12 | DA21-11 |  | <0.009 | clear | 179 | 700 | none | 8.16 | none | 0.12 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-08-14 | DA21-12 |  | <0.009 | clear | 183 | 701 | none | 8.2 | none | 0.17 | 0 | 0
Zone 1- MC estate, Castle Hosue | 2019-08-21 | DA21-13 |  | <0.009 | clear | 175 | 727 | none | 8.02 | none | 0.13 | 0 | 0
Zone 2-LL - Line Wall, Gib Oil | 2019-08-21 | DA21-14 |  | <0.009 | clear | 173 | 710 | none | 8.12 | none | 0.11 | 0 | 0
Zone 3-ED- Europa point toilets | 2019-08-21 | DA21-15 |  | <0.009 | clear | 182 | 758 | none | 8.18 | none | 0.17 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-08-21 | DA21-16 |  | <0.009 | clear | 183 | 738 | none | 8.19 | none | 0.09 | 0 | 0
Zone 1- South District, New Harbours | 2019-08-27 | DA21-17 |  | 0.011 | clear | 188 | 771 | none | 8.11 | none | 0.14 | 0 | 0
Zone 2-LL - King's Bastion Leisure Centre, 55 Line Wall Road | 2019-08-27 | DA21-18 |  | <0.009 | clear | 180 | 715 | none | 8.11 | none | 0.12 | 0 | 0
Zone 3-ED- Clifftons | 2019-08-27 | DA21-19 |  | <0.009 | clear | 211 | 824 | none | 8.19 | none | 0.13 | 0 | 0
Zone 4- Upper rock, WWll tunnels | 2019-08-27 | DA21-20 |  | <0.009 | clear | 193 | 767 | none | 8.09 | none | 0.16 | 0 | 0
Zone1 - South District, 7 Coelho House | 2019-09-04 | DS10-1 |  | <0.009 | clear | 228 | 830 | none | 7.98 | none | 0.22 | 0 | 0
Zone2-LL- Piazza | 2019-09-04 | DS10-2 |  | <0.009 | clear | 189 | 779 | none | 8.08 | none | 0.17 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-09-04 | DS10-3 |  | <0.009 | clear | 220 | 836 | none | 8.11 | none | 0.13 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2019-09-04 | DS10-4 |  | <0.009 | clear | 218 | 847 | none | 8.1 | none | 0.16 | 0 | 0
Zone 1- Shipping, Waterport, Gib Oil office | 2019-09-11 | DS10-5 |  | <0.009 | clear | 179 | 803 | none | 8.02 | none | 0.14 | 0 | 0
Zone 2-LL - John Mackintosh Hall | 2019-09-11 | DS10-6 |  | <0.009 | clear | 186 | 804 | none | 7.79 | none | 0.23 | 0 | 0
Zone 3-ED- Sunset Close | 2019-09-11 | DS10-7 |  | <0.009 | clear | 193 | 827 | none | 7.96 | none | 0.15 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-09-11 | DS10-8 |  | <0.009 | clear | 209 | 829 | none | 8.01 | none | 0.09 | 0 | 0
Zone 1- Westside, Morrisons Supermarket | 2019-09-17 | DS10-9 |  | <0.009 | clear | 199 | 747 | none | 8.01 | none | 0.12 | 0 | 0
Zone 2-LL - Casemates | 2019-09-17 | DS10-10 |  | <0.009 | clear | 190 | 794 | none | 8.06 | none | 0.19 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-09-17 | DS10-11 |  | <0.009 | clear | 186 | 759 | none | 7.91 | none | 0.17 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-09-17 | DS10-12 |  | <0.009 | clear | 161 | 688 | none | 8.02 | none | 0.16 | 0 | 0
Zone 1- North Front, Beach View Terraces | 2019-09-26 | DS10-13 |  | <0.009 | clear | 194 | 795 | none | 8.05 | none | 0.16 | 0 | 0
Zone 2-LL - Piazza | 2019-09-26 | DS10-14 |  | <0.009 | clear | 206 | 800 | none | 8.07 | none | 0.18 | 0 | 0
Zone 3-ED- The Clifftons | 2019-09-26 | DS10-15 |  | <0.009 | clear | 217 | 823 | none | 8.13 | none | 0.11 | 0 | 0
Zone 4- Upper Rock, Poca Rocca | 2019-09-26 | DS10-16 |  | <0.009 | clear | 228 | 850 | none | 8.04 | none | 0.21 | 0 | 0
Zone1 - Moorish Castle Estate, | 2019-10-01 | DO10-1 |  | <0.009 | clear | 214 | 834 | none | 8.1 | none | 0.14 | 0 | 0
Zone2-LL- Line Wall Road, Gib Oil petrol station | 2019-10-01 | DO10-2 |  | <0.009 | clear | 197 | 804 | none | 8.04 | none | 0.1 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-10-01 | DO10-3 |  | <0.009 | clear | 205 | 923 | none | 8.1 | none | 0.18 | 0 | 0
Zone 4 - Upper Rock, WWII Tunnels | 2019-10-01 | DO10-4 |  | <0.009 | clear | 203 | 856 | none | 8.14 | none | 0.22 | 0 | 0
Zone 1- High Level, Leanse Place, AquaGib office kitchen | 2019-10-08 | DO10-5 |  | <0.009 | clear | 194 | 764 | none | 8.01 | none | 0.14 | 0 | 0
Zone 2-LL - Midtown carpark | 2019-10-08 | DO10-6 |  | <0.009 | clear | 204 | 773 | none | 8.06 | none | 0.19 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-10-08 | DO10-7 |  | <0.009 | clear | 187 | 764 | none | 8.06 | none | 0.16 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2019-10-08 | DO10-8 |  | <0.009 | clear | 209 | 766 | none | 8.1 | none | 0.09 | 0 | 0
Zone 1- South District, AquaGib Ragged Staff depot | 2019-10-14 | DO10-9 |  | <0.009 | clear | 200 | 756 | none | 8.01 | none | 0.16 | 0 | 0
Zone 2-LL - ICC toilets | 2019-10-14 | DO10-10 |  | <0.009 | clear | 198 | 777 | none | 8.04 | none | 0.12 | 0 | 0
Zone 3-ED- The Clifftons | 2019-10-16 | DO10-11 |  | <0.009 | clear | 185 | 762 | none | 8.09 | none | 0.14 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-10-16 | DO10-12 |  | <0.009 | clear | 180 | 820 | none | 7.99 | none | 0.09 | 0 | 0
Zone 1- Westside, Eurotowers, Timeout Café | 2019-10-23 | DO10-13 |  | <0.009 | clear | 199 | 761 | none | 8.01 | none | 0.14 | 0 | 0
Zone 2-LL - Castle Road, The Care Agency Elderly Home | 2019-10-21 | DO10-14 |  | <0.009 | clear | 170 | 751 | none | 8.16 | none | 0.14 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-10-23 | DO10-15 |  | <0.009 | clear | 190 | 754 | none | 7.99 | none | 0.18 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-10-21 | DO10-16 |  | <0.009 | clear | 169 | 765 | none | 8.06 | none | 0.18 | 0 | 0
Zone 1- Westside, GASA swimming pool | 2019-10-30 | DO10-17 |  | <0.009 | clear | 174 | 750 | none | 8.1 | none | 0.16 | 0 | 0
Zone 2-LL - John Mackintosh Hall | 2019-10-30 | DO10-18 |  | <0.009 | clear | 182 | 768 | none | 8 | none | 0.12 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-10-30 | DO10-19 |  | <0.009 | clear | 184 | 751 | none | 7.97 | none | 0.14 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2019-10-30 | DO10-20 |  | <0.009 | clear | 185 | 753 | none | 8.06 | none | 0.2 | 0 | 0
Zone1 - North Front, Glacis Estate, Glacis Kiosk | 2019-11-04 | DN10-1 |  | <0.009 | clear | 171 | 728 | none | 8.07 | none | 0.14 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2019-11-06 | DN10-2 |  | <0.009 | clear | 183 | 744 | none | 8.01 | none | 0.14 | 0 | 0
Zone 3-ED- The Clifftons | 2019-11-04 | DN10-3 |  | <0.009 | clear | 186 | 741 | none | 8.22 | none | 0.18 | 0 | 0
Zone 4 - Upper Rock, Jews Gate | 2019-11-06 | DN10-4 |  | <0.009 | clear | 178 | 714 | none | 8.01 | none | 0.15 | 0 | 0
Zone 1- High Level, Tank Ramp | 2019-11-11 | DN10-5 |  | <0.009 | clear | 152 | 712 | none | 8.06 | none | 0.14 | 0 | 0
Zone 2-LL - Piazza Fountain | 2019-11-11 | DN10-6 |  | <0.009 | clear | 175 | 727 | none | 8.08 | none | 0.13 | 0 | 0
Zone 3-ED- Alectoris Lane, Sacarellos | 2019-11-11 | DN10-7 |  | <0.009 | clear | 158 | 712 | none | 8.09 | none | 0.17 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm sample tap | 2019-11-11 | DN10-8 |  | <0.009 | clear | 170 | 714 | none | 8.08 | none | 0.1 | 0 | 0
Zone 1- South District, Piccadily Restaurant | 2019-11-20 | DN10-9 |  | <0.009 | clear | 178 | 710 | none | 8.22 | none | 0.14 | 0 | 0
Zone 2-LL - Kings Bastion Leisure Centre | 2019-11-20 | DN10-10 |  | <0.009 | clear | 179 | 721 | none | 8.23 | none | 0.1 | 0 | 0
Zone 3-ED- Europa Point toilets | 2019-11-20 | DN10-11 |  | <0.009 | clear | 162 | 716 | none | 8.18 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2019-11-20 | DN10-12 |  | <0.009 | clear | 171 | 731 | none | 8.31 | none | 0.18 | 0 | 0
Zone 1- Shipping, AquaGib, Distiller depot | 2019-11-25 | DN10-13 |  | <0.009 | clear | 160 | 745 | none | 8.07 | none | 0.1 | 0 | 0
Zone 2-LL - ICC toilets | 2019-11-27 | DN10-14 |  | <0.009 | clear | 188 | 728 | none | 8.06 | none | 0.14 | 0 | 0
Zone 3-ED- Eliotts Battery | 2019-11-27 | DN10-15 |  | <0.009 | clear | 203 | 712 | none | 8.03 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2019-11-25 | DN10-16 |  | <0.009 | clear | 163 | 727 | none | 8.02 | none | 0.13 | 0 | 0
Zone1 - Westside, St Bernard's Hospital | 2019-12-04 | DD10-1 |  | <0.009 | clear | 163 | 704 | none | 8.06 | none | 0.13 | 0 | 0
Zone2-LL- Piazza | 2019-12-04 | DD10-2 |  | <0.009 | clear | 176 | 726 | none | 8.18 | none | 0.11 | 0 | 0
Zone 3-ED- The Clifftons | 2019-12-04 | DD10-3 |  | <0.009 | clear | 172 | 669 | none | 8.09 | none | 0.22 | 0 | 0
Zone 4 - Upper Rock, Poca Rocca | 2019-12-04 | DD10-4 |  | <0.009 | clear | 162 | 704 | none | 8.15 | none | 0.15 | 0 | 0
Zone 1- Moorish Castle Estate, Olly's takeaway | 2019-12-12 | DD10-5 |  | <0.009 | clear | 136 | 699 | none | 8.03 | none | 0.23 | 0 | 0
Zone 2-LL - Midtown carpark | 2019-12-12 | DD10-6 |  | <0.009 | clear | 147 | 736 | none | 7.95 | none | 0.12 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-12-12 | DD10-7 |  | <0.009 | clear | 141 | 706 | none | 7.97 | none | 0.18 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2019-12-12 | DD10-8 |  | <0.009 | clear | 159 | 697 | none | 8.06 | none | 0.14 | 0 | 0
Zone 1- Moorish Castle Estate, | 2019-12-18 | DD10-9 |  | <0.009 | clear | 171 | 715 | none | 8.04 | none | 0.16 | 0 | 0
Zone 2-LL - Midtown carpark | 2019-12-18 | DD10-10 |  | <0.009 | clear | 167 | 713 | none | 8.05 | none | 0.1 | 0 | 0
Zone 3-ED- Highcliffe House | 2019-12-18 | DD10-11 |  | <0.009 | clear | 172 | 712 | none | 8.1 | none | 0.13 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2019-12-18 | DD10-12 |  | <0.009 | clear | 163 | 707 | none | 8.04 | none | 0.18 | 0 | 0
Zone1 - High Level, Town Range, Senior Citizens club | 2020-01-08 | DJ33-1 |  | <0.009 | clear | 175 | 699 | none | 8.15 | none | 0.23 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2020-01-06 | DJ33-2 |  | <0.009 | clear | 181 | 700 | none | 8.13 | none | 0.17 | 0 | 0
Zone 3-ED- Europa Point toilets | 2020-01-06 | DJ33-3 |  | <0.009 | clear | 182 | 717 | none | 8.22 | none | 0.13 | 0 | 0
Zone 4 - Upper Rock, Upper Galleries | 2020-01-06 | DJ33-4 |  | <0.009 | clear | 184 | 713 | none | 8.19 | none | 0.09 | 0 | 0
Zone 1- High Level, New Harbours, Oxy Ltd | 2020-01-15 | DJ33-5 |  | <0.009 | clear | 186 | 711 | none | 8.12 | none | 0.11 | 0 | 0
Zone 2-LL - Line Wall Road, Gib Oil | 2020-01-13 | DJ33-6 |  | <0.009 | clear | 159 | 718 | none | 8.06 | none | 0.13 | 0 | 0
Zone 3-ED- Cliffton Mews | 2020-01-15 | DJ33-7 |  | <0.009 | clear | 181 | 710 | none | 8.16 | none | 0.13 | 0 | 0
Zone 4- Upper rock, Devil's Gap | 2020-01-15 | DJ33-8 |  | <0.009 | clear | 186 | 717 | none | 8.1 | none | 0.14 | 0 | 0
Zone 1- Westside, McDonalds | 2020-01-23 | DJ33-9 |  | <0.009 | clear | 217 | 723 | none | 8.26 | none | 0.13 | 0 | 0
Zone 2-LL - ICC toilets | 2020-01-23 | DJ33-10 |  | <0.009 | clear | 206 | 715 | none | 8.14 | none | 0.14 | 0 | 0
Zone 3-ED- Highcliffe House | 2020-01-23 | DJ33-11 |  | <0.009 | clear | 204 | 710 | none | 8.12 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Poca Rocca | 2020-01-23 | DJ33-12 |  | <0.009 | clear | 202 | 722 | none | 8.17 | none | 0.15 | 0 | 0
Zone 1- North Front, MOT Centre, Devil's Tower Road | 2020-01-30 | DJ33-13 |  | <0.009 | clear | 214 | 670 | none | 8.09 | none | 0.19 | 0 | 0
Zone 2-LL - John Mcintosh Hall | 2020-01-30 | DJ33-14 |  | <0.009 | clear | 206 | 681 | none | 8.1 | none | 0.12 | 0 | 0
Zone 3-ED- Bleak House | 2020-01-30 | DJ33-15 |  | <0.009 | clear | 199 | 623 | none | 7.93 | none | 0.09 | 0 | 0
Zone 4- Upper rock, WWII Tunnels | 2020-01-30 | DJ33-16 |  | <0.009 | clear | 204 | 704 | none | 8.02 | none | 0.07 | 0 | 0
Zone1 - South District, New Harbours Industrial Estate, 101 Gibraltar | 2020-02-06 | DJ33-1 |  | <0.009 | clear | 196 | 748 | none | 8.16 | none | 0.12 | 0 | 0
Zone2-LL- Gibraltar Chronicle, Line Wall Road | 2020-02-06 | DJ33-2 |  | <0.009 | clear | 180 | 744 | none | 8.06 | none | 0.16 | 0 | 0
Zone 3-ED- Eliotts Battery | 2020-02-06 | DJ33-3 |  | <0.009 | clear | 189 | 766 | none | 8.06 | none | 0.14 | 0 | 0
Zone 4 - Upper Rock, Lower Bruces Farm | 2020-02-06 | DJ33-4 |  | <0.009 | clear | 207 | 721 | none | 7.95 | none | 0.11 | 0 | 0
Zone 1- Shipping, Waterport Terraces, Day Centre | 2020-02-12 | DJ33-5 |  | <0.009 | clear | 188 | 721 | none | 8.18 | none | 0.14 | 0 | 0
Zone 2-LL - Castle Road, The Care Agency Elderly Home | 2020-02-12 | DJ33-6 |  | <0.009 | clear | 196 | 725 | none | 8.11 | none | 0.13 | 0 | 0
Zone 3-ED- Sacarellos, Alectoris Lane | 2020-02-12 | DJ33-7 |  | <0.009 | clear | 163 | 661 | none | 8.14 | none | 0.18 | 0 | 0
Zone 4- Upper rock, Upper Galleries | 2020-02-12 | DJ33-8 |  | <0.009 | clear | 184 | 726 | none | 8.23 | none | 0.15 | 0 | 0
Zone 1- High Level, 57 Willis' Road, Little Learner's nursery | 2020-02-19 | DJ33-9 |  | <0.009 | clear | 197 | 772 | none | 8.17 | none | 0.11 | 0 | 0
Zone 2-LL - Gibraltar Chronicle, Line Wall Road | 2020-02-17 | DJ33-10 |  | <0.009 | clear | 189 | 722 | none | 8.18 | none | 0.13 | 0 | 0
Zone 3-ED- Eliotts Battery | 2020-02-19 | DJ33-11 |  | <0.009 | clear | 204 | 814 | none | 8.16 | none | 0.15 | 0 | 0
Zone 4- Upper rock, Lower Bruces Farm | 2020-02-17 | DJ33-12 |  | <0.009 | clear | 188 | 758 | none | 8.24 | none | 0.14 | 0 | 0
Zone 1- Westside, Queensway, Ragged Staff meter box | 2020-02-24 | DJ33-13 |  | <0.009 | clear | 189 | 740 | none | 8.22 | none | 0.19 | 0 | 0
Zone 2-LL - King's Bastion Leisure Centre, 55 Line Wall Road | 2020-02-26 | DJ33-14 |  | <0.009 | clear | 194 | 738 | none | 8.17 | none | 0.11 | 0 | 0
Zone 3-ED- The Clifftons | 2020-02-24 | DJ33-15 |  | <0.009 | clear | 190 | 715 | none | 8.23 | none | 0.11 | 0 | 0
Zone 4- Upper rock, Moorish Castle tourist site | 2020-02-26 | DJ33-16 |  | <0.009 | clear | 183 | 726 | none | 8.18 | none | 0.1 | 0 | 0
Zone 1- North Front, unit 8 Gustavo Bacarisa House, Glacis Estate | 2020-03-05 | DM22-1 |  | <0.009 | clear | 194 | 716 | none | 8.18 | none | 0.11 | <1 Not Detected | <1 Not Detected
Zone2-LL- Gib Oil, Line Wall Road | 2020-03-03 | DM22-2 |  | <0.009 | clear | 159 | 732 | none | 8.04 | none | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Highcliffe House | 2020-03-05 | DM22-3 |  | <0.009 | clear | 191 | 710 | none | 8.21 | none | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock, WWII Tunnels | 2020-03-03 | DM22-4 |  | <0.009 | clear | 177 | 727 | none | 8.01 | none | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1- South District, New Harbours, Gibtelecom depot | 2020-03-12 | DM22-5 |  | <0.009 | clear | 177 | 716 | none | 8.14 | none | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2-LL - Casemates | 2020-03-12 | DM22-6 |  | <0.009 | clear | 199 | 725 | none | 8.11 | none | 0.1 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Bleak House | 2020-03-12 | DM22-7 |  | <0.009 | clear | 184 | 701 | none | 8.37 | none | 0.09 | <1 Not Detected | <1 Not Detected
Zone 4- Upper rock, lower Bruce's Farm sample tap | 2020-03-12 | DM22-8 |  | <0.009 | clear | 191 | 733 | none | 8.27 | none | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1- South District, Alameda Gardens, public toilet | 2020-07-14 | DJ35-1 |  | <0.009 | clear | 203 | 749 | none | 8.16 | none | 0.29 | <1 Not Detected | <1 Not Detected
Zone 2-LL - Pet Zone, Bishop Rapallo's Ramp | 2020-07-14 | DJ35-2 |  | <0.009 | clear | 193 | 730 | none | 8.13 | none | 0.3 | <1 Not Detected | <1 Not Detected
Zone 3-ED- The Clifftons | 2020-07-14 | DJ35-3 |  | <0.009 | clear | 205 | 766 | none | 8.28 | none | 0.34 | <1 Not Detected | <1 Not Detected
Zone 4- Upper rock, Upper Galleries | 2020-07-14 | DJ35-4 |  | <0.009 | clear | 197 | 758 | none | 8.29 | none | 0.24 | <1 Not Detected | <1 Not Detected
Zone 1- Moorish Castle Estate, shop | 2020-07-17 | DJ35-5 |  | <0.009 | clear | 190 | 722 | none | 8.22 | none | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2-LL - Gib Oil, Line Wall Road | 2020-07-17 | DJ35-6 |  | <0.009 | clear | 188 | 700 | none | 8.19 | none | 0.1 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Highcliffe House | 2020-07-17 | DJ35-7 |  | <0.009 | clear | 202 | 827 | none | 8.34 | none | 0.07 | <1 Not Detected | <1 Not Detected
Zone 4- Upper rock, Devil's Gap | 2020-07-17 | DJ35-8 |  | <0.009 | clear | 200 | 742 | none | 8.24 | none | 0.09 | <1 Not Detected | <1 Not Detected
Zone 1- Shipping, AquaGib, Distiller depot | 2020-07-21 | DJ35-9 |  | <0.009 | clear | 208 | 792 | none | 8.12 | none | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2-LL - Town Range, Rock on the Rock Club | 2020-07-21 | DJ35-10 |  | <0.009 | clear | 194 | 747 | none | 8.18 | none | 0.13 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Block 21, Eliotts Battery | 2020-07-23 | DJ35-11 |  | <0.009 | clear | 221 | 827 | none | 8.25 | none | 0.25 | <1 Not Detected | <1 Not Detected
Zone 4- Upper rock, Lower Bruces Farm sample tap | 2020-07-21 | DJ35-12 |  | <0.009 | clear | 221 | 811 | none | 8.32 | none | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1- High Level, Leanse Place, AquaGib Main Office | 2020-07-29 | DJ35-13 |  | <0.009 | clear | 238 | 798 | none | 8.07 | none | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2-LL - Midtown coachpark terminal | 2020-07-31 | DJ35-14 |  | <0.009 | clear | 257 | 795 | none | 8.02 | none | 0.09 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Europa Point toilets | 2020-07-29 | DJ35-15 |  | <0.009 | clear | 235 | 843 | none | 8.19 | none | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4- Upper rock, WWII Tunnels tourist site | 2020-07-31 | DJ35-16 |  | <0.009 | clear | 219 | 794 | none | 8.11 | none | 0.19 | <1 Not Detected | <1 Not Detected
Zone1 - Westside, GASA swimming pool | 2020-08-06 | DA23-1 |  | <0.009 | clear | 176 | 769 | none | 8.02 | none | 0.18 | <1 Not Detected | <1 Not Detected
Zone2-LL- John Mackintosh Hall | 2020-08-06 | DA23-2 |  | <0.009 | clear | 192 | 773 | none | 7.95 | none | 0.15 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Bleak House | 2020-08-06 | DA23-3 |  | <0.009 | clear | 191 | 738 | none | 8.14 | none | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock, Devil's Gap | 2020-08-06 | DA23-4 |  | <0.009 | clear | 194 | 765 | none | 8.16 | none | 0.2 | <1 Not Detected | <1 Not Detected
Zone 1- North Front, Caleta lifeguard post | 2020-08-11 | DA23-5 |  | <0.009 | clear | 206 | 748 | none | 7.49 | none | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2-LL - ICC toilets | 2020-08-13 | DA23-6 |  | <0.009 | clear | 198 | 772 | none | 8 | none | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Clifftons | 2020-08-11 | DA23-7 |  | 0.018 | clear | 223 | 828 | none | 8.16 | none | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4- Upper rock, Upper Galleries | 2020-08-13 | DA23-8 |  | <0.009 | clear | 226 | 848 | none | 8.17 | none | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1- New Harbours DHL | 2020-08-20 | DA23-9 |  | <0.009 | clear | 217 | 742 | none | 8.1 | none | 0.29 | <1 Not Detected | <1 Not Detected
Zone 2- Piazza Toilets | 2020-08-20 | DA23-10 |  | <0.009 | clear | 222 | 766 | none | 8.03 | none | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3- The Clifftons | 2020-08-20 | DA23-11 |  | <0.009 | clear | 198 | 720 | none | 8.17 | none | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4- Devils Gap | 2020-08-20 | DA23-12 |  | <0.009 | clear | 189 | 728 | none | 8.16 | none | 0.33 | <1 Not Detected | <1 Not Detected
Zone 1- HL- Police Barracks | 2020-08-27 | DA23-13 |  | <0.009 | clear | 196 | 708 | none | 7.39 | none | 0.7 | <1 Not Detected | <1 Not Detected
Zone 2-LL - Bristol Hotel | 2020-08-27 | DA23-14 |  | <0.009 | clear | 203 | 771 | none | 8.1 | none | 0.15 | <1 Not Detected | <1 Not Detected
Zone 3-ED- Top of Naval Hospital | 2020-08-27 | DA23-15 |  | <0.009 | clear | 185 | 723 | none | 8.16 | none | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock Pocca Rocca | 2020-08-27 | DA23-16 |  | <0.009 | clear | 199 | 779 | none | 8.09 | none | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1- NF - Bay Fabrication | 2021-05-06 | D2021-05-1 |  | <0.009 | Clear | 195 | 767 | None | 8.11 | None | 0.37 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - Casemates Toilets | 2021-05-06 | D2021-05-2 |  | <0.009 | Clear | 202 | 773 | None | 8.06 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - Sunset Close | 2021-05-06 | D2021-05-3 |  | <0.009 | Clear | 212 | 818 | None | 8.09 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Moorish Castle Tourist Site | 2021-05-06 | D2021-05-4 |  | <0.009 | Clear | 225 | 851 | None | 8.06 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1- Shipping Flying Angel | 2021-05-13 | D2021-05-5 |  | <0.009 | Clear | 202 | 786 | None | 8.21 | None | 0.55 | <1 Not Detected | <1 Not Detected
Zone 2- LL- Leanse Place | 2021-05-13 | D2021-05-6 |  | <0.009 | Clear | 196 | 726 | None | 7.96 | None | 0.4 | <1 Not Detected | <1 Not Detected
Zone 3 - ED - Cliffton | 2021-05-13 | D2021-05-7 |  | <0.009 | Clear | 235 | 850 | None | 8.75 | None | 0.43 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Upper Gallery | 2021-05-13 | D2021-05-8 |  | <0.009 | Clear | 239 | 870 | None | 8.42 | None | 0.49 | <1 Not Detected | <1 Not Detected
Zone 1- HL - Carters | 2021-05-19 | D2021-05-9 |  | <0.009 | Clear | 193 | 749 | None | 7.96 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 -LL - John Macintosh Hall Toilets | 2021-05-19 | D2021-05-10 |  | <0.009 | Clear | 198 | 764 | None | 8.01 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - ED - Elderly Care | 2021-05-19 | D2021-05-11 |  | <0.009 | Clear | 181 | 703 | None | 8.06 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Lathbury Toilets | 2021-05-19 | D2021-05-12 |  | <0.009 | Clear | 186 | 718 | None | 8.09 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 1- WP - W.P.R.O Toilets | 2021-05-27 | D2021-05-13 |  | <0.009 | Clear | 198 | 728 | None | 7.86 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 2- Piazza Toilets | 2021-05-27 | D2021-05-14 |  | <0.009 | Clear | 196 | 753 | None | 8.03 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3- Sunset Close | 2021-05-27 | D2021-05-15 |  | <0.009 | Clear | 200 | 766 | None | 7.97 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Moorish Castle Tourist Site | 2021-05-27 | D2021-05-16 |  | <0.009 | Clear | 198 | 791 | None | 8.02 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1- WP - Gib Oil Stores North Mole | 2021-06-01 | D2021-06-1 |  | <0.009 | Clear | 194.7 | 782 | None | 7.74 | None | 0.63 | <1 Not Detected | <1 Not Detected
Zone 2- LL- Casemates Toilets | 2021-06-01 | D2021-06-2 |  | <0.009 | Clear | 196.47 | 786 | None | 7.81 | None | 0.7 | <1 Not Detected | <1 Not Detected
Zone 3- The Clifftons | 2021-06-01 | D2021-06-3 |  | <0.009 | Clear | 208.86 | 843 | None | 7.84 | None | 0.39 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Pocca Rocca | 2021-06-01 | D2021-06-4 |  | <0.009 | Clear | 203.55 | 837 | None | 8.03 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 1 - NF - Toilets | 2021-06-01 | D2021-06-5 |  | <0.009 | Clear | 205 | 821 | None | 7.87 | None | 0.72 | <1 Not Detected | <1 Not Detected
Zone 2- LL- Social Club | 2021-06-01 | D2021-06-6 |  | <0.009 | Clear | 202 | 813 | None | 7.85 | None | 0.55 | <1 Not Detected | <1 Not Detected
Zone 3 - Brymtons - Binstore | 2021-06-01 | D2021-06-7 |  | <0.009 | Clear | 204 | 844 | None | 7.79 | None | 0.4 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2021-06-01 | D2021-06-8 |  | <0.009 | Clear | 175 | 832 | None | 7.86 | None | 0.37 | <1 Not Detected | <1 Not Detected
Zone 1-SD - Shipping - M&E | 2021-06-17 | D2021-06-9 |  | <0.009 | Clear | 207 | 787 | None | 7.87 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 2-LL- Wesley Pharmacy | 2021-06-17 | D2021-06-10 |  | <0.009 | Clear | 202 | 771 | None | 7.86 | None | 0.5 | <1 Not Detected | <1 Not Detected
Zone 3- Highcliff | 2021-06-17 | D2021-06-11 |  | <0.009 | Clear | 202 | 764 | None | 7.93 | None | 0.41 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Upper Gallery | 2021-06-17 | D2021-06-12 |  | <0.009 | Clear | 198 | 788 | None | 8 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 1-WS- College Clinic Toilet | 2021-06-24 | D2021-06-13 |  | <0.009 | Clear | 230 | 916 | None | 7.97 | None | 0.44 | <1 Not Detected | <1 Not Detected
Zone 2 -LL- ICC Toilets | 2021-06-24 | D2021-06-14 |  | <0.009 | Clear | 209 | 842 | None | 7.9 | None | 0.97 | <1 Not Detected | <1 Not Detected
Zone 3 Ocean Views Mental Health Toilet | 2021-06-24 | D2021-06-15 |  | <0.009 | Clear | 234 | 954 | None | 8.06 | None | 0.53 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Devil's Gap | 2021-06-24 | D2021-06-16 |  | <0.009 | Clear | 232 | 929 | None | 8.1 | None | 0.8 | <1 Not Detected | <1 Not Detected
Zone 1- SD - Rock Hotel | 2021-07-01 | D2021-07-1 |  | <0.009 | Clear | 212 | 837 | None | 7.98 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - John Mackintosh Hall Toilets | 2021-07-01 | D2021-07-2 |  | <0.009 | Clear | 219 | 856 | None | 8.03 | None | 0.58 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliff | 2021-07-01 | D2021-07-3 |  | <0.009 | Clear | 195 | 761 | None | 7.87 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2021-07-01 | D2021-07-4 |  | <0.009 | Clear | 193 | 781 | None | 8.05 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Victoria Stadium | 2021-11-02 | D2021-11-1 |  | <0.009 | Clear | 186 | 709 | None | 7.65 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 2 - City Mill Lane | 2021-11-02 | D2021-11-2 |  | <0.009 | Clear | 195 | 742 | None | 7.99 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mews | 2021-11-02 | D2021-11-3 |  | <0.009 | Clear | 196 | 754 | None | 7.78 | None | 0.37 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- Bruce's Farm | 2021-11-02 | D2021-11-4 |  | <0.009 | Clear | 193 | 749 | None | 8 | None | 0.49 | <1 Not Detected | <1 Not Detected
Zone 1- Rock Hotel | 2021-11-11 | D2021-11-5 |  | <0.009 | Clear | 191 | 713 | None | 7.69 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 2 - John Mackintosh Hall Toilets | 2021-11-11 | D2021-11-6 |  | <0.009 | Clear | 191 | 728 | None | 7.85 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliftons | 2021-11-11 | D2021-11-7 |  | <0.009 | Clear | 188 | 730 | None | 7.73 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Poca Roca | 2021-11-11 | D2021-11-8 |  | <0.009 | Clear | 198 | 763 | None | 7.98 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 1 - College Clinic Toilets | 2021-11-18 | D2021-11-9 |  | <0.009 | Clear | 200 | 692 | None | 7.86 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC Toilets | 2021-11-18 | D2021-11-10 |  | <0.009 | Clear | 182 | 704 | None | 7.84 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliff House | 2021-11-18 | D2021-11-11 |  | <0.009 | Clear | 181 | 700 | None | 7.71 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock - Moorish Castle Tourist Site | 2021-11-18 | D2021-11-12 |  | <0.009 | Clear | 184 | 699 | None | 7.81 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 1 - The Caleta Hotel | 2021-11-25 | D2021-11-13 |  | <0.009 | Clear | 181 | 700 | None | 7.74 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 -Chatham Counter Guard Toilet | 2021-11-25 | D2021-11-14 |  | <0.009 | Clear | 181 | 693 | None | 7.86 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Views Terraces House | 2021-11-25 | D2021-11-15 |  | <0.009 | Clear | 173 | 673 | None | 7.71 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Devil's Gap | 2021-11-25 | D2021-11-16 |  | <0.009 | Clear | 181 | 692 | None | 7.94 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 1 - SD - 19 Victoria House, Alemeda Estate | 2021-09-03 | D2021-09-1 |  | <0.009 | Clear | 208 | 813 | None | 7.78 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2 - WP toilets M&E | 2021-09-03 | D2021-09-2 |  | <0.009 | Clear | 214 | 826 | None | 7.78 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe House | 2021-09-03 | D2021-09-3 |  | <0.009 | Clear | 202 | 784 | None | 7.88 | None | 0.06 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- Moorish Castle Tourist Site | 2021-09-03 | D2021-09-4 |  | <0.009 | Clear | 203 | 794 | None | 7.87 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1- Leanse Place | 2021-09-08 | D2021-09-5 |  | <0.009 | Clear | 211 | 815 | None | 7.72 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2- LL- Eureka Emilio Butcher | 2021-09-08 | D2021-09-6 |  | <0.009 | Clear | 211 | 811 | None | 7.71 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3- Brympton Bin Store | 2021-09-08 | D2021-09-7 |  | <0.009 | Clear | 206 | 813 | None | 7.86 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Devil's Gap | 2021-09-08 | D2021-09-8 |  | <0.009 | Clear | 202 | 793 | None | 7.89 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1 - College Clinic | 2021-09-16 | D2021-09-9 |  | <0.009 | Clear | 203 | 730 | None | 7.73 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 2-LL- John Macintosh Hall Toilets | 2021-09-16 | D2021-09-10 |  | <0.009 | Clear | 213 | 788 | None | 7.69 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3- Highcliff | 2021-09-16 | D2021-09-11 |  | <0.009 | Clear | 206 | 754 | None | 7.76 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Hay's level Tunnel Toilets | 2021-09-16 | D2021-09-12 |  | <0.009 | Clear | 196 | 814 | None | 7.81 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 1 - Flying Angel Bar | 2021-09-23 | D2021-09-13 |  | <0.009 | Clear | 193 | 754 | None | 7.75 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - John Mackintosh Sqaure Toilets | 2021-09-23 | D2021-09-14 |  | <0.009 | Clear | 196 | 768 | None | 7.7 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftons House | 2021-09-23 | D2021-09-15 |  | <0.009 | Clear | 191 | 744 | None | 7.66 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Bruce's Farm | 2021-09-23 | D2021-09-16 |  | <0.009 | Clear | 202 | 776 | None | 7.79 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1- Rock Hotel Toilets | 2021-09-30 | D2021-09-17 |  | <0.009 | Clear | 193 | 760 | None | 7.6 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Counter Guard Toilets | 2021-09-30 | D2021-09-18 |  | <0.009 | Clear | 195 | 762 | None | 7.68 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilet | 2021-09-30 | D2021-09-19 |  | <0.009 | Clear | 189 | 751 | None | 7.54 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2021-09-30 | D2021-09-20 |  | <0.009 | Clear | 207 | 801 | None | 7.78 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 1 - Flat Bastion Road | 2021-10-05 | D2021-10-1 |  | <0.009 | Clear | 204 | 779 | None | 7.73 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion Toilets | 2021-10-05 | D2021-10-2 |  | <0.009 | Clear | 212 | 762 | None | 7.66 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 3 - Lynx Club | 2021-10-05 | D2021-10-3 |  | <0.009 | Clear | 189 | 748 | None | 7.56 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- Moorish Castle Tourist Site | 2021-10-05 | D2021-10-4 |  | <0.009 | Clear | 214 | 810 | None | 7.78 | None | 0.42 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2021-10-14 | D2021-10-5 |  | <0.009 | Clear | 189 | 735 | None | 7.94 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - Waterport Terraces Bin Store | 2021-10-14 | D2021-10-6 |  | <0.009 | Clear | 175 | 683 | None | 7.98 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftons | 2021-10-14 | D2021-10-7 |  | <0.009 | Clear | 193 | 765 | None | 7.79 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Hay's Level Tunnel Toilets | 2021-10-14 | D2021-10-8 |  | <0.009 | Clear | 181 | 698 | None | 8.09 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1 - Alemeda Toilets | 2021-10-21 | D2021-10-9 |  | <0.009 | Clear | 189 | 715 | None | 7.78 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 2 -LL- John Macintosh Hall Toilets | 2021-10-21 | D2021-10-10 |  | <0.009 | Clear | 186 | 697 | None | 7.92 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Elliots Battery | 2021-10-21 | D2021-10-11 |  | <0.009 | Clear | 188 | 727 | None | 7.89 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- Poca Roca | 2021-10-21 | D2021-10-12 |  | <0.009 | Clear | 188 | 725 | None | 7.98 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1-WS- College Clinic Toilet | 2021-10-28 | D2021-10-13 |  | <0.009 | Clear | 184 | 710 | None | 7.91 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 -LL- ICC Toilets | 2021-10-28 | D2021-10-14 |  | <0.009 | Clear | 191 | 722 | None | 7.91 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe Binstore | 2021-10-28 | D2021-10-15 |  | <0.009 | Clear | 196 | 760 | None | 7.79 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2021-10-28 | D2021-10-16 |  | <0.009 | Clear | 189 | 728 | None | 7.94 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 1 - NF - The Caleta Palace | 2021-07-08 | D2021-07-1 |  | <0.010 | Clear | 195 | 781 | None | 8.08 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 - LL- Chatham Counterguard Toilets | 2021-07-08 | D2021-07-2 |  | <0.011 | Clear | 207 | 821 | None | 8.03 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2021-07-08 | D2021-07-3 |  | <0.012 | Clear | 189 | 749 | None | 7.89 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2021-07-08 | D2021-07-4 |  | <0.013 | Clear | 181 | 720 | None | 8.11 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 1 - John Mac | 2021-07-15 | D2021-07-5 |  | <0.009 | Clear | 204 | 797 | None | 7.94 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion Leisure Center | 2021-07-15 | D2021-07-6 |  | <0.009 | Clear | 204 | 799 | None | 8.01 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - University Halls | 2021-07-15 | D2021-07-7 |  | <0.009 | Clear | 193 | 748 | Slight Chlorine | 7.87 | Slight Chlorine | 0.2 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2021-07-15 | D2021-07-8 |  | <0.009 | Clear | 196 | 785 | None | 8.07 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2021-07-22 | D2021-07-9 |  | <0.009 | Clear | 199 | 766 | None | 7.81 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - John Mackintosh square Toilets | 2021-07-22 | D2021-07-10 |  | <0.009 | Clear | 200 | 772 | None | 7.86 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - Lathbury Industrial Park | 2021-07-22 | D2021-07-11 |  | <0.009 | Clear | 188 | 731 | Slight Chlorine | 7.75 | Slight Chlorine | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Bruce's Farm | 2021-07-22 | D2021-07-12 |  | <0.009 | Clear | 192 | 758 | None | 8 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - NF - Victoria Stadium Toilets | 2021-07-27 | D2021-07-13 |  | <0.009 | Clear | 201 | 781 | None | 7.94 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - London Bar | 2021-07-27 | D2021-07-14 |  | <0.009 | Clear | 199 | 788 | None | 7.88 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe | 2021-07-27 | D2021-07-15 |  | <0.009 | Clear | 191 | 751 | Slight Chlorine | 7.84 | Slight Chlorine | 0.37 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Devil's Gap | 2021-07-27 | D2021-07-16 |  | <0.009 | Clear | 184 | 736 | None | 8.03 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1 - College Clinic Toilets | 2021-12-02 | D2021-12-1 |  | <0.009 | Clear | 172 | 672 | None | 7.83 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC Toilets | 2021-12-02 | D2021-12-2 |  | <0.009 | Clear | 181 | 683 | None | 7.76 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe House | 2021-12-02 | D2021-12-3 |  | <0.009 | Clear | 173 | 679 | None | 7.69 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- Moorish Castle Tourist Site | 2021-12-02 | D2021-12-4 |  | <0.009 | Clear | 170 | 673 | None | 7.75 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 1- Shipping - Flying Angel Club | 2021-12-09 | D2021-12-5 |  | <0.009 | Clear | 170 | 661 | None | 8.01 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 2- LL- King's Bastion Toilets | 2021-12-09 | D2021-12-6 |  | <0.009 | Clear | 171 | 677 | None | 7.84 | None | 0.39 | <1 Not Detected | <1 Not Detected
Zone 3- Brympton Bin Stores | 2021-12-09 | D2021-12-7 |  | <0.009 | Clear | 181 | 707 | None | 7.73 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Poca Roca | 2021-12-09 | D2021-12-8 |  | <0.009 | Clear | 164 | 647 | None | 7.87 | None | 0.42 | <1 Not Detected | <1 Not Detected
Zone 1-SD - College Clinic | 2021-12-16 | D2021-12-9 |  | <0.009 | Clear | 172 | 668 | None | 7.76 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 2-LL- ICC Toilets | 2021-12-16 | D2021-12-10 |  | <0.009 | Clear | 168 | 660 | None | 7.67 | None | 0.4 | <1 Not Detected | <1 Not Detected
Zone 3- Highcliff | 2021-12-16 | D2021-12-11 |  | <0.009 | Clear | 182 | 704 | None | 7.71 | None | 0.48 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Moorish Castle Tourist Site | 2021-12-16 | D2021-12-12 |  | <0.009 | Clear | 181 | 669 | None | 7.75 | None | 0.55 | <1 Not Detected | <1 Not Detected
Zone 1- Coaling Island Marina | 2021-12-23 | D2021-12-13 |  | <0.009 | Clear | 172 | 653 | None | 7.6 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 2 -John Mackintosh hall toilets | 2021-12-23 | D2021-12-14 |  | <0.009 | Clear | 172 | 655 | None | 7.63 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mews | 2021-12-23 | D2021-12-15 |  | <0.009 | Clear | 175 | 695 | None | 7.62 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- Hay's Level Tunnel | 2021-12-23 | D2021-12-16 |  | <0.009 | Clear | 170 | 655 | None | 7.69 | None | 0.4 | <1 Not Detected | <1 Not Detected
Zone 1- NF - Victoria Stadium Toilets | 2021-12-29 | D2021-12-17 |  | <0.009 | Clear | 172 | 653 | None | 7.71 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 2- Piazza Toilets | 2021-12-29 | D2021-12-18 |  | <0.009 | Clear | 172 | 654 | None | 7.67 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 3- Clifftons | 2021-12-29 | D2021-12-19 |  | <0.009 | Clear | 186 | 695 | None | 7.63 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Bruce's Farm | 2021-12-29 | D2021-12-20 |  | <0.009 | Clear | 175 | 679 | None | 7.79 | None | 0.41 | <1 Not Detected | <1 Not Detected
Zone 1 - College Clinic Toilets | 2021-08-05 | D2021-08-1 |  | <0.009 | Clear | 192 | 789 | None | 7.91 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 -LL- ICC Toilets | 2021-08-05 | D2021-08-2 |  | <0.009 | Clear | 194 | 790 | None | 0.84 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - The Clifftons | 2021-08-05 | D2021-08-3 |  | <0.009 | Clear | 187 | 761 | Slight Chlorine | 7.8 | Slight Chlorine | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Moorish Castle Tourist Site | 2021-08-05 | D2021-08-4 |  | <0.009 | Clear | 199 | 815 | None | 7.98 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - SD - Rock Hotel | 2021-08-12 | D2021-08-5 |  | <0.009 | Clear | 210 | 773 | None | 7.96 | None | 0.54 | <1 Not Detected | <1 Not Detected
Zone 2 - LL- John Mackintosh Hall Toilets | 2021-08-12 | D2021-08-6 |  | <0.009 | Clear | 202 | 755 | None | 7.98 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 3 - Lathbury Industrial Park | 2021-08-12 | D2021-08-7 |  | <0.009 | Clear | 183 | 728 | Slight Chlorine | 7.9 | Slight Chlorine | 0.37 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Hay's Level | 2021-08-12 | D2021-08-8 |  | <0.009 | Clear | 219 | 756 | None | 7.96 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 1-SD - Coviran Toilets | 2021-08-19 | D2021-08-9 |  | <0.009 | Clear | 202 | 826 | None | 7.81 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 2-LL- John Macintosh Hall Toilets | 2021-08-19 | D2021-08-10 |  | <0.009 | Clear | 198 | 804 | None | 7.85 | None | 0.72 | <1 Not Detected | <1 Not Detected
Zone 3- Highcliff | 2021-08-19 | D2021-08-11 |  | <0.009 | Clear | 180 | 755 | None | 7.81 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Moorish Castle Tourist Site | 2021-08-19 | D2021-08-12 |  | <0.009 | Clear | 183 | 756 | None | 7.98 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone1 - Westside - District 41 - Small Boats Marina | 2022-04-05 | D2022-04-1 |  | <0.009 | Clear | 226 | 691 | None | 7.78 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - King's Bastion Leisure center | 2022-04-05 | D2022-04-2 |  | <0.009 | Clear | 214 | 723 | None | 7.67 | None | 0.81 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2022-04-05 | D2022-04-3 |  | <0.009 | Clear | 180 | 714 | None | 7.75 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Upper Galleries | 2022-04-05 | D2022-04-4 |  | <0.009 | Clear | 204 | 742 | None | 7.75 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone1 - Shipping - Waterport M&E | 2022-05-13 | D2022-05-1 |  | <0.009 | Clear | 200 | 823 | None | 7.98 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - District 8 - Bristol Hotel | 2022-05-13 | D2022-05-2 |  | <0.009 | Slight Brown | 230 | 823 | None | 7.79 | None | 2.38 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2022-05-13 | D2022-05-3 |  | <0.009 | Clear | 234 | 804 | None | 7.87 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Hay's Level Tunnel | 2022-05-13 | D2022-05-4 |  | <0.009 | Clear | 190 | 785 | None | 7.83 | None | 0.44 | <1 Not Detected | <1 Not Detected
Zone1 - North Front - D23 - Constitution house | 2022-05-20 | D2022-05-5 |  | <0.009 | Clear | 182 | 760 | None | 7.82 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - D10 - Gib Oil Petrol Station | 2022-05-20 | D2022-05-6 |  | <0.009 | Clear | 190 | 809 | None | 7.74 | None | 0.59 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe | 2022-05-20 | D2022-05-7 |  | <0.009 | Clear | 216 | 744 | None | 7.75 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Poca Roca | 2022-05-20 | D2022-05-8 |  | <0.009 | Clear | 222 | 753 | None | 7.83 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - District 14 - Senior Citizens club | 2022-05-26 | D2022-05-9 |  | <0.009 | Clear | 236 | 791 | None | 7.75 | None | 0.72 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - District 11 - Calpe Hounds | 2022-05-26 | D2022-05-10 |  | <0.009 | Clear | 220 | 799 | None | 7.82 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2022-05-26 | D2022-05-11 |  | <0.009 | Clear | 196 | 742 | None | 7.73 | None | 0.09 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2022-05-26 | D2022-05-12 |  | <0.009 | Clear | 196 | 754 | None | 7.94 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone1 - South District - District 15 - The Rock Hotel | 2022-05-31 | D2022-05-13 |  | <0.009 | Clear | n/a | 731 | None | 7.6 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - District 6 - Gib Oil Line Wall Road | 2022-05-31 | D2022-05-14 |  | <0.009 | Clear | n/a | 759 | None | 7.54 | None | 0.39 | <1 Not Detected | <1 Not Detected
Zone 3 - The Clifftons | 2022-05-31 | D2022-05-15 |  | <0.009 | Clear | n/a | 739 | None | 7.64 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Bruce's Farm | 2022-05-31 | D2022-05-16 |  | <0.009 | Clear | n/a | 718 | None | 7.68 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - NF - Victoria Stadium Toilets | 2022-02-03 | D2022-02-1 |  | <0.009 | Clear | 205 | 761 | None | 7.87 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - John Mackintosh Hall Toilets | 2022-02-03 | D2022-02-2 |  | <0.009 | Clear | 219 | 817 | None | 7.86 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Views terraces | 2022-02-03 | D2022-02-3 |  | <0.009 | Clear | 204 | 774 | None | 8.05 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2022-02-03 | D2022-02-4 |  | <0.009 | Clear | 202 | 778 | None | 8.03 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1- Waterport Terraces | 2022-02-10 | D2022-02-5 |  | <0.009 | Clear | 188 | 720 | None | 7.66 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2- LL- City Mill Lane | 2022-02-10 | D2022-02-6 |  | <0.009 | Clear | 225 | 860 | None | 7.81 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe house | 2022-02-10 | D2022-02-7 |  | <0.009 | Clear | 184 | 737 | None | 7.85 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Hay's Level tunnel | 2022-02-10 | D2022-02-8 |  | <0.009 | Clear | 189 | 769 | None | 7.9 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1- Small Boats Marina | 2022-02-17 | D2022-02-9 |  | <0.009 | Clear | 189 | 722 | None | 7.89 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 2 -LL- ICC Toilets | 2022-02-17 | D2022-02-10 |  | <0.009 | Clear | 216 | 801 | None | 7.84 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 3- Brympton Binstore | 2022-02-17 | D2022-02-11 |  | <0.009 | Clear | 186 | 734 | None | 7.94 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Moorish Castle Tourist Site | 2022-02-17 | D2022-02-12 |  | <0.009 | Clear | 196 | 765 | None | 8.02 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone1 - Shipping - Flying Angel | 2022-06-09 | D2022-06-1 |  | <0.009 | Clear |  | 762 | None | 7.63 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - Kings bastion | 2022-06-09 | D2022-06-2 |  | <0.009 | Clear |  | 744 | None | 7.65 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point | 2022-06-09 | D2022-06-3 |  | <0.009 | Clear |  | 749 | None | 7.66 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Hay's Level Tunnel | 2022-06-09 | D2022-06-4 |  | <0.009 | Clear |  | 761 | None | 7.71 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone1 - Victoria Stadium | 2022-06-16 | D2022-06-5 |  | <0.009 | Clear |  | 784 | None | 7.42 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - O'Callaghan Hotel | 2022-06-16 | D2022-06-6 |  | <0.009 | Clear |  | 781 | None | 7.39 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2022-06-16 | D2022-06-7 |  | <0.009 | Clear |  | 799 | None | 7.57 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Upper Galleries | 2022-06-16 | D2022-06-8 |  | <0.009 | Clear |  | 841 | None | 7.67 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone1 - North Front - D28 - Catalan Bay | 2022-06-23 | D2022-06-9 |  | <0.009 | Clear |  | 850 | None | 7.73 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - D11 - City Mill Lane | 2022-06-23 | D2022-06-10 |  | <0.009 | Clear |  | 820 | None | 7.68 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa view Terraces | 2022-06-23 | D2022-06-11 |  | <0.009 | Clear |  | 786 | None | 7.63 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Devil's Gap | 2022-06-23 | D2022-06-12 |  | <0.009 | Clear |  | 840 | None | 7.81 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone1 - High level - District 13 - Carters Shop | 2022-06-30 | D2022-06-13 |  | <0.009 | Clear | 178 | 683 | None | 7.83 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - District 6 - Chatham Toilets | 2022-06-30 | D2022-06-14 |  | <0.009 | Clear | 205 | 796 | None | 7.63 | None | 0.46 | <1 Not Detected | <1 Not Detected
Zone 3 - Sunset Close | 2022-06-30 | D2022-06-15 |  | <0.009 | Clear | 184 | 702 | None | 7.7 | None | 0.49 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Bruce's Farm | 2022-06-30 | D2022-06-16 |  | <0.009 | Clear | 192 | 709 | None | 7.73 | None | 0.43 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel Club | 2022-03-03 | D2022-03-1 |  | <0.009 | Clear | 238 | 742 | None | 7.91 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion Toilets | 2022-03-03 | D2022-03-2 |  | <0.009 | Clear | 217 | 772 | None | 7.99 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton Binstore | 2022-03-03 | D2022-03-3 |  | <0.009 | Clear | 231 | 832 | None | 8.04 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Great Siege Tunnels Toilets | 2022-03-03 | D2022-03-4 |  | <0.009 | Clear | 217 | 791 | None | 8.05 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1- Waterport terraces | 2022-03-17 | D2022-03-5 |  | <0.009 | Clear | 189 | 724 | None | 7.74 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2- LL- City Mill Lane | 2022-03-17 | D2022-03-6 |  | <0.009 | Clear | 195 | 760 | None | 7.76 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3- Highcluffe House | 2022-03-17 | D2022-03-7 |  | <0.009 | Clear | 189 | 742 | None | 7.78 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Hay's level Tunnel | 2022-03-17 | D2022-03-8 |  | <0.009 | Clear | 186 | 737 | None | 7.82 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1-NF - Victoria Stadium | 2022-03-24 | D2022-03-9 |  | <0.009 | Clear | 198 | 755 | None | 7.39 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2-LL- John Macintosh Hall Toilets | 2022-03-24 | D2022-03-10 |  | <0.009 | Clear | 193 | 744 | None | 7.78 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3- Europa Point Toilets | 2022-03-24 | D2022-03-11 |  | <0.009 | Clear | 196 | 757 | None | 7.86 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Bruce's Farm | 2022-03-24 | D2022-03-12 |  | <0.009 | Clear | 189 | 728 | None | 7.85 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - Waterport Terraces | 2022-01-18 | D2022-01-1 |  | <0.009 | Clear | 182 | 698 | None | 7.88 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall toilets | 2022-01-18 | D2022-01-2 |  | <0.009 | Clear | 179 | 690 | None | 7.86 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe | 2022-01-20 | D2022-01-3 |  | <0.009 | Clear | 175 | 690 | None | 7.95 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock- 9 Poca Roca | 2022-01-18 | D2022-01-4 |  | <0.009 | Clear | 177 | 701 | None | 7.92 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 1- SD - New Harbour Industrial park | 2022-01-25 | D2022-01-5 |  | <0.009 | Clear | 195 | 791 | None | 7.9 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2- LL- Chatham toilets | 2022-01-25 | D2022-01-6 |  | <0.009 | Clear | 190 | 731 | None | 7.89 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 3- Europa point | 2022-01-25 | D2022-01-7 |  | <0.009 | Clear | 192 | 806 | None | 8.02 | None | 0.76 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Hay's Level Tunnel | 2022-01-25 | D2022-01-8 |  | <0.009 | Clear | 196 | 801 | None | 8 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1 - 16 Willis Passage | 2022-04-05 | D2022-04-1 |  | <0.009 | Clear | 226 | 691 | None | 7.78 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion Toilets | 2022-04-05 | D2022-04-2 |  | <0.009 | Clear | 214 | 723 | None | 7.67 | None | 0.81 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton Binstore | 2022-04-05 | D2022-04-3 |  | <0.009 | Clear | 180 | 714 | None | 7.75 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Great Siege Tunnels Toilets | 2022-04-05 | D2022-04-4 |  | <0.009 | Clear | 204 | 742 | None | 7.75 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1-NF - Victoria Stadium | 2022-04-12 | D2022-04-5 |  | <0.009 | Clear | 194 | 715 | None | 7.65 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2- LL- London Bar | 2022-04-12 | D2022-04-6 |  | <0.009 | Clear | 201 | 945 | None | 7.71 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 3- Europa View Terraces | 2022-04-12 | D2022-04-7 |  | <0.009 | Clear | 267 | 730 | None | 7.68 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4- Upper Rock- Hay's level Tunnel | 2022-04-12 | D2022-04-8 |  | <0.009 | Clear | 202 | 730 | None | 7.67 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1- Shipping - Flying Angel Club | 2022-04-21 | D2022-04-9 |  | <0.009 | Clear | 193 | 689 | None | 7.67 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - ICC Toilets | 2022-04-19 | D2022-04-10 |  | <0.009 | Brown | 201 | 776 | None | 7.83 | None | 3.84 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe House | 2022-04-21 | D2022-04-11 |  | <0.009 | Clear | 208 | 736 | None | 7.67 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Lower Bruce's Farm | 2022-04-21 | D2022-04-12 |  | <0.009 | Clear | 192 | 740 | None | 7.75 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1- SD - Rock Hotel | 2022-04-28 | D2022-04-13 |  | <0.009 | Clear | 220 | 762 | None | 7.45 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 2 - LL- John Mackintosh Hall Toilets | 2022-04-19 | D2022-04-14 |  | <0.009 | Clear | 212 | 752 | None | 7.61 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 3 - Elliots Battery | 2022-04-28 | D2022-04-15 |  | <0.009 | Clear | 201 | 783 | None | 7.61 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2022-04-28 | D2022-04-16 |  | <0.009 | Clear | 230 | 822 | None | 7.66 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone1 - Rock Hotel | 2022-07-15 | D2022-07-1 |  | <0.009 | Clear | 200 | 705 | None | 7.43 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - Ombudsman | 2022-07-15 | D2022-07-2 |  | <0.009 | Clear | 188 | 738 | None | 7.49 | None | 0.69 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2022-07-15 | D2022-07-3 |  | <0.009 | Clear | 191 | 718 | None | 7.62 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Poca Roca | 2022-07-15 | D2022-07-4 |  | <0.009 | Clear | 192 | 713 | None | 7.71 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone1 - Waterport Desalination | 2022-07-19 | D2022-07-5 |  | <0.009 | Clear | 190 | 722 | None | 7.47 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - Bristol Hotel | 2022-07-19 | D2022-07-6 |  | <0.009 | Clear | 187 | 724 | None | 7.65 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 3 - Buena Vista Park Villas | 2022-07-19 | D2022-07-7 |  | <0.009 | Clear | 193 | 745 | None | 7.75 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Hay's Level Tunnel | 2022-07-19 | D2022-07-8 |  | <0.009 | Clear | 192 | 750 | None | 7.7 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone1 - Varyl Begg Estate | 2022-07-29 | D2022-07-9 |  | <0.009 | Clear | 195 | 709 | None | 7.54 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - LL - Chatham Toilets | 2022-07-29 | D2022-07-10 |  | <0.009 | Clear | 194 | 733 | None | 7.63 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Toilets | 2022-07-29 | D2022-07-11 |  | <0.009 | Clear | 224 | 746 | None | 8.03 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Rock - Upper Galleries | 2022-07-29 | D2022-07-12 |  | <0.009 | Clear | 201 | 729 | None | 7.95 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Waterport Plant | 2023-01-04 | D2023-01-1 |  | <0.009 | Clear | 186 | 781 | None | 8.36 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 2 - Gib Oil Line wall road | 2023-01-04 | D2023-01-2 |  | <0.009 | Clear | 194 | 692 | None | 7.77 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - HighCliffe House | 2023-01-04 | D2023-01-3 |  | <0.009 | Clear | 170 | 643 | None | 7.92 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-01-04 | D2023-01-4 |  | <0.009 | Clear | 184 | 659 | None | 7.84 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Waterport Terraces | 2023-01-11 | D2023-01-5 |  | <0.009 | Clear | 198 | 758 | None | 8.16 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2023-01-11 | D2023-01-6 |  | <0.009 | Clear | 198 | 711 | None | 7.97 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2023-01-11 | D2023-01-7 |  | <0.009 | Clear | 176 | 674 | None | 8.03 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-01-11 | D2023-01-8 |  | <0.009 | Clear | 180 | 660 | None | 7.85 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front Cemetery Road | 2023-01-16 | D2023-01-9 |  | <0.009 | Clear | 190 | 684 | None | 7.86 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Bus Stop | 2023-01-16 | D2023-01-10 |  | <0.009 | Clear | 189 | 703 | None | 7.9 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2023-01-16 | D2023-01-11 |  | <0.009 | Clear | 187 | 734 | None | 7.87 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-01-16 | D2023-01-12 |  | <0.009 | Clear | 183 | 764 | None | 7.76 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Rock on the Rock | 2023-01-25 | D2023-01-13 |  | <0.009 | Clear | 175 | 688 | None | 7.98 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - Marina Bay | 2023-01-25 | D2023-01-14 |  | <0.009 | Clear | 180 | 689 | None | 8.13 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Sports Complex | 2023-01-25 | D2023-01-15 |  | <0.009 | Clear | 173 | 669 | None | 8.16 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-01-25 | D2023-01-16 |  | <0.009 | Clear | 190 | 717 | None | 8.05 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Victoria Stadium | 2023-02-02 | D2023-02-1 |  | <0.009 | Clear | 182 | 704 | None | 8.2 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2023-02-02 | D2023-02-2 |  | <0.009 | Clear | 191 | 695 | None | 8.07 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-02-02 | D2023-02-3 |  | <0.009 | Clear | 180 | 705 | None | 8.07 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-02-02 | D2023-02-4 |  | <0.009 | Clear | 177 | 690 | None | 8.1 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Rock Hotel | 2023-02-08 | D2023-02-5 |  | <0.009 | Clear | 190 | 698 | None | 8.01 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 2 - City Mill Lane | 2023-02-08 | D2023-02-6 |  | <0.009 | Clear | 192 | 692 | None | 8.17 | None | 0.48 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe House | 2023-02-08 | D2023-02-7 |  | <0.009 | Clear | 152 | 609 | None | 8.1 | None | 0.6 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-02-08 | D2023-02-8 |  | <0.009 | Clear | 167 | 626 | None | 8.2 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Waterport Plant | 2023-02-15 | D2023-02-9 |  | <0.009 | Clear | 204 | 735 | None | 8.19 | None | 0.42 | <1 Not Detected | <1 Not Detected
Zone 2 - Bristol Hotel | 2023-02-15 | D2023-02-10 |  | <0.009 | Clear | 182 | 702 | None | 8.53 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2023-02-15 | D2023-02-11 |  | <0.009 | Clear | 183 | 730 | None | 8.17 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-02-15 | D2023-02-12 |  | <0.009 | Clear | 186 | 719 | None | 8.15 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Small Boats Marina | 2023-02-22 | D2023-02-13 |  | <0.009 | Clear | 198 | 711 | None | 8.09 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - Piazza toilets | 2023-02-22 | D2023-02-14 |  | <0.009 | Clear | 200 | 716 | None | 7.92 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2023-02-22 | D2023-02-15 |  | <0.009 | Clear | 190 | 709 | None | 7.95 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Great Siege Tunnels | 2023-02-22 | D2023-02-16 |  | <0.009 | Clear | 193 | 708 | None | 7.66 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Leanse's Place | 2023-03-01 | D2023-03-1 |  | <0.009 | Clear | 187 | 698 | None | 6.93 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2023-03-01 | D2023-03-2 |  | <0.009 | Clear | 190 | 713 | None | 7.89 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-03-01 | D2023-03-3 |  | <0.009 | Clear | 173 | 660 | None | 7.86 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-03-01 | D2023-03-4 |  | <0.009 | Clear | 175 | 671 | None | 7.89 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Cepsa | 2023-03-06 | D2023-03-5 |  | <0.009 | Clear | 182 | 682 | None | 8 | None | 0.43 | <1 Not Detected | <1 Not Detected
Zone 2 - Irish Town (Coviran) | 2023-03-06 | D2023-03-6 |  | <0.009 | Clear | 189 | 691 | None | 7.95 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - The Clifftons | 2023-03-06 | D2023-03-7 |  | <0.009 | Clear | 153 | 675 | None | 7.99 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-03-06 | D2023-03-8 |  | <0.009 | Clear | 179 | 686 | None | 7.82 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2023-03-15 | D2023-03-9 |  | <0.009 | Clear | 189 | 715 | None | 8.08 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 2 - Marina Bay | 2023-03-15 | D2023-03-10 |  | <0.009 | Clear | 181 | 701 | None | 8.04 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2023-03-15 | D2023-03-11 |  | <0.009 | Clear | 189 | 722 | None | 7.84 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-03-15 | D2023-03-12 |  | <0.009 | Clear | 190 | 711 | None | 7.94 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Morrisons | 2023-03-22 | D2023-03-13 |  | <0.009 | Clear | 185 | 708 | None | 7.83 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2023-03-22 | D2023-03-14 |  | <0.009 | Clear | 180 | 724 | None | 7.88 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2023-03-22 | D2023-03-15 |  | <0.009 | Clear | 187 | 744 | None | 8.07 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-03-22 | D2023-03-16 |  | <0.009 | Clear | 186 | 739 | None | 8.07 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - New Harbours | 2023-03-29 | D2023-03-17 |  | <0.009 | Clear | 198 | 693 | None | 7.92 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - Zoca Tavern | 2023-03-29 | D2023-03-18 |  | <0.009 | Clear | 174 | 699 | None | 7.89 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 3 - The Mount | 2023-03-29 | D2023-03-19 |  | <0.009 | Clear | 177 | 713 | None | 7.84 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-03-29 | D2023-03-20 |  | <0.009 | Clear | 170 | 690 | None | 7.88 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Senior Citizens Club | 2023-04-03 | D2023-04-1 |  | <0.009 | Clear | 179 | 706 | None | 7.11 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 2 - Angry Frier | 2023-04-03 | D2023-04-2 |  | <0.009 | Clear | 178 | 714 | None | 7.18 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3 - HighCliffe House | 2023-04-03 | D2023-04-3 |  | 0.015 | Clear | 174 | 655 | None | 7.16 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-04-03 | D2023-04-4 |  | 0.017 | Clear | 170 | 683 | None | 7.18 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Shop | 2023-04-13 | D2023-04-5 |  | <0.009 | Clear | 176 | 678 | None | 8.16 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 2 - World Trade Center | 2023-04-13 | D2023-04-6 |  | <0.009 | Clear | 176 | 698 | None | 8.07 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2023-04-13 | D2023-04-7 |  | <0.009 | Clear | 158 | 640 | None | 8.01 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-04-13 | D2023-04-8 |  | <0.009 | Clear | 178 | 671 | None | 7.82 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Ocean Village | 2023-04-18 | D2023-04-9 |  | <0.009 | Clear | 180 | 694 | None | 7.86 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 2 - Irish Town 84 Meter Box | 2023-04-17 | D2023-04-10 |  | <0.009 | Clear | 189 | 688 | None | 7.99 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Meter Box | 2023-04-17 | D2023-04-11 |  | <0.009 | Clear | 171 | 677 | None | 8.09 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-04-18 | D2023-04-12 |  | <0.009 | Clear | 159 | 664 | None | 7.94 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2023-04-25 | D2023-04-13 |  | <0.009 | Clear | 181 | 694 | None | 8.12 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2023-04-25 | D2023-04-14 |  | <0.009 | Clear | 176 | 682 | None | 8 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-04-25 | D2023-04-15 |  | <0.009 | Clear | 235 | 928 | None | 7.79 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-04-25 | D2023-04-16 |  | <0.009 | Clear | 278 | 1062 | None | 7.84 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Holiday Inn Hotel | 2023-05-03 | D2023-05-1 |  | <0.009 | Clear | 193 | 731 | None | 7.93 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2023-05-03 | D2023-05-2 |  | <0.009 | Clear | 192 | 752 | None | 7.95 | None | 0.46 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Halls | 2023-05-03 | D2023-05-3 |  | <0.009 | Clear | 194 | 706 | None | 8.08 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-05-03 | D2023-05-4 |  | <0.009 | Clear | 175 | 693 | None | 8.03 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - 4 Stagioni | 2023-05-09 | D2023-05-5 |  | <0.009 | Clear | 200 | 718 | None | 8.03 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 2 - Strands Hairdresser | 2023-05-09 | D2023-05-6 |  | <0.009 | Clear | 183 | 724 | None | 7.86 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University | 2023-05-09 | D2023-05-7 |  | <0.009 | Clear | 185 | 709 | None | 8.09 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den Toilets | 2023-05-09 | D2023-05-8 |  | <0.009 | Clear | 206 | 724 | None | 8.01 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Carters | 2023-05-17 | D2023-05-9 |  | <0.009 | Clear | 178 | 727 | None | 7.99 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 - PickWick's Bistro | 2023-05-17 | D2023-05-10 |  | <0.009 | Clear | 195 | 747 | None | 7.93 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2023-05-17 | D2023-05-11 |  | <0.009 | Clear | 176 | 677 | None | 7.96 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-05-17 | D2023-05-12 |  | <0.009 | Clear | 193 | 712 | None | 7.77 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Comorant Wharf | 2023-05-24 | D2023-05-13 |  | <0.009 | Clear | 184 | 682 | None | 8 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - Venture inn Pub | 2023-05-24 | D2023-05-14 |  | <0.009 | Clear | 186 | 720 | None | 7.77 | None | 0.93 | <1 Not Detected | <1 Not Detected
Zone 3 - Naval Hospital Hill (Straits View) | 2023-05-24 | D2023-05-15 |  | <0.009 | Clear | 174 | 595 | None | 8.07 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-05-24 | D2023-05-16 |  | <0.009 | Clear | 189 | 668 | None | 8 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 3 - Naval Hospital Hill (Straits View) | 2023-05-30 | D2023-05-17 |  | <0.009 | Clear | 177 | 675 | None | 7.98 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-05-30 | D2023-05-18 |  | <0.009 | Clear | 168 | 647 | None | 8.06 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Waterport Plant | 2023-06-01 | D2023-06-1 |  | <0.009 | Clear | 184 | 693 | None | 8.08 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2023-06-01 | D2023-06-2 |  | <0.009 | Clear | 182 | 688 | None | 7.77 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Shop | 2023-06-09 | D2023-06-3 |  | <0.009 | Clear | 178 | 715 | None | 7.96 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2023-06-09 | D2023-06-4 |  | <0.009 | Clear | 168 | 680 | None | 7.9 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2023-06-09 | D2023-06-5 |  | <0.009 | Clear | 239 | 787 | None | 7.88 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-06-09 | D2023-06-6 |  | <0.009 | Clear | 206 | 739 | None | 7.86 | None | 0.09 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Varel Begg | 2023-06-14 | D2023-06-7 |  | <0.009 | Clear | 203 | 761 | None | 7.89 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - Ragged Staff Aquagib Depot | 2023-06-12 | D2023-06-8 |  | <0.009 | Clear | 192 | 706 | None | 7.87 | None | 0.75 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliffton's | 2023-06-14 | D2023-06-9 |  | <0.009 | Clear | 200 | 708 | None | 7.87 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-06-14 | D2023-06-10 |  | <0.009 | Clear | 196 | 727 | None | 7.91 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Victoria Stadium (Cepsa) | 2023-06-22 | D2023-06-11 |  | <0.009 | Clear | 198 | 745 | None | 7.97 | None | 0.44 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Square Toilets | 2023-06-22 | D2023-06-12 |  | <0.009 | Clear | 186 | 723 | None | 7.93 | None | 0.44 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-06-22 | D2023-06-13 |  | <0.009 | Clear | 187 | 705 | None | 7.89 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-06-22 | D2023-06-14 |  | <0.009 | Clear | 195 | 722 | None | 7.99 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 1 - South Distric - Alemeda Gardens | 2023-06-29 | D2023-06-15 |  | <0.009 | Clear | 201 | 784 | None | 7.96 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 2 - Angry Frier | 2023-06-29 | D2023-06-16 |  | <0.009 | Clear | 195 | 750 | None | 8.03 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2023-06-29 | D2023-06-17 |  | <0.009 | Clear | 203 | 779 | None | 8.07 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-06-29 | D2023-06-18 |  | <0.009 | Clear | 209 | 772 | None | 8.03 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - AquaGib M&E Depot | 2023-07-05 | D2023-07-1 |  | <0.009 | Clear | 190 | 758 | None | 8 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - 3 Owls | 2023-07-05 | D2023-07-2 |  | <0.009 | Clear | 202 | 747 | None | 7.8 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar Uni Halls | 2023-07-05 | D2023-07-3 |  | <0.009 | Clear | 192 | 756 | None | 8.05 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-07-05 | D2023-07-4 |  | <0.009 | Clear | 191 | 744 | None | 8.04 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 -Moorish Castle estate - Calpe House | 2023-07-10 | D2023-07-5 |  | <0.009 | Clear | 189 | 742 | None | 8.14 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2023-07-10 | D2023-07-6 |  | <0.009 | Clear | 200 | 742 | None | 7.83 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 3 - The Mount | 2023-07-10 | D2023-07-7 |  | <0.009 | Clear | 188 | 733 | None | 8.07 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovey's Cottage | 2023-07-10 | D2023-07-8 |  | <0.009 | Clear | 183 | 740 | None | 8.09 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2023-08-02 | D2023-08-1 |  | <0.009 | Clear | 189 | 734 | None | 8.13 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2023-08-02 | D2023-08-2 |  | <0.009 | Clear | 192 | 742 | None | 7.97 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-08-02 | D2023-08-3 |  | <0.009 | Clear | 176 | 717 | None | 7.96 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2023-08-02 | D2023-08-4 |  | <0.009 | Clear | 176 | 686 | None | 7.95 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Morrisons | 2023-08-09 | D2023-08-5 |  | <0.009 | Clear | 200 | 747 | None | 7.74 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - Ragged Staff Aquagib Depot | 2023-08-09 | D2023-08-6 |  | <0.009 | Clear | 170 | 714 | None | 8.01 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliftons | 2023-08-09 | D2023-08-7 |  | <0.009 | Clear | 185 | 693 | None | 7.95 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-08-09 | D2023-08-8 |  | <0.009 | Clear | 186 | 703 | None | 8.04 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Calatal Bay Toilets | 2023-08-16 | D2023-08-9 |  | 0.036 | Clear | 203 | 786 | None | 7.92 | None | 0.26 | 1 | <1 Not Detected
Zone 2 - Midtown The Little Kitchen | 2023-08-16 | D2023-08-10 |  | 0.036 | Clear | 219 | 818 | None | 7.86 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University | 2023-08-16 | D2023-08-11 |  | 0.036 | Clear | 198 | 775 | None | 8.03 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den Toilets | 2023-08-16 | D2023-08-12 |  | <0.009 | Clear | 199 | 749 | None | 8.09 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Senior Citizens Club | 2023-08-30 | D2023-08-13 |  | <0.009 | Clear | 190 | 690 | None | 7.9 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2023-08-30 | D2023-08-14 |  | <0.009 | Clear | 196 | 699 | None | 7.9 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliftons | 2023-08-30 | D2023-08-15 |  | <0.009 | Clear | 196 | 701 | None | 8.07 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-08-30 | D2023-08-16 |  | <0.009 | Clear | 207 | 743 | None | 8.08 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Varel Begg Nursery | 2023-09-07 | D2023-09-1 |  | <0.009 | Clear | 208 | 775 | None | 7.72 | None | 0.05 | <1 Not Detected | <1 Not Detected
Zone 2 - Marina Bay | 2023-09-07 | D2023-09-2 |  | <0.009 | Clear | 209 | 773 | None | 8.06 | None | 0.05 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2023-09-07 | D2023-09-3 |  | <0.009 | Clear | 199 | 750 | None | 8.01 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2023-09-07 | D2023-09-4 |  | <0.009 | Clear | 198 | 749 | None | 7.99 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2023-09-13 | D2023-09-5 |  | <0.009 | Clear | 212 | 761 | None | 8.22 | None | 0.53 | <1 Not Detected | <1 Not Detected
Zone 2 - Wesley Pharmacy | 2023-09-13 | D2023-09-6 |  | <0.009 | Clear | 193 | 701 | None | 8.14 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-09-13 | D2023-09-7 |  | <0.009 | Clear | 219 | 764 | None | 8.05 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-09-13 | D2023-09-8 |  | <0.009 | Clear | 222 | 763 | None | 8.07 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Shop | 2023-09-20 | D2023-09-9 |  | <0.009 | Clear | 174 | 682 | None | 7.96 | None | 0.5 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2023-09-20 | D2023-09-10 |  | <0.009 | Clear | 196 | 672 | None | 7.77 | None | 0.63 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Halls | 2023-09-20 | D2023-09-11 |  | <0.009 | Clear | 182 | 598 | None | 8.03 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovey's Cottage | 2023-09-20 | D2023-09-12 |  | <0.009 | Clear | 182 | 606 | None | 7.98 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Laguna Bar | 2023-09-28 | D2023-09-13 |  | <0.009 | Clear | 222 | 736 | None | 8.09 | None | 0.48 | <1 Not Detected | <1 Not Detected
Zone 2 - Bristol Hotel | 2023-09-28 | D2023-09-14 |  | <0.009 | Clear | 206 | 710 | None | 7.86 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2023-09-28 | D2023-09-15 |  | <0.009 | Clear | 192 | 692 | None | 7.86 | None | 0.08 | <1 Not Detected | <1 Not Detected
Zone 4 - Eroski | 2023-09-28 | D2023-09-16 |  | <0.009 | Clear | 176 | 678 | None | 7.91 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2023-10-05 | D2023-10-1 |  | <0.009 | Clear | 162 | 671 | None | 8.2 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Bus Stop | 2023-10-05 | D2023-10-2 |  | <0.009 | Clear | 177 | 695 | None | 8.02 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 3 - HighCliffe House | 2023-10-05 | D2023-10-3 |  | <0.009 | Clear | 188 | 719 | None | 8 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-10-05 | D2023-10-4 |  | <0.009 | Clear | 189 | 701 | None | 8.02 | None | 0.49 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - 102 Watergarderns | 2023-10-11 | D2023-10-5 |  | <0.009 | Clear | 207 | 818 | None | 7.77 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion LC | 2023-10-11 | D2023-10-6 |  | <0.009 | Clear | 185 | 715 | None | 7.86 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliftons | 2023-10-11 | D2023-10-7 |  | <0.009 | Clear | 176 | 698 | None | 7.93 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-10-11 | D2023-10-8 |  | <0.009 | Clear | 176 | 664 | None | 8.04 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Rosia Vet | 2023-10-16 | D2023-10-9 |  | <0.009 | Clear | 195 | 711 | None | 7.93 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 2 - Engineer's Lane | 2023-10-16 | D2023-10-10 |  | <0.009 | Slight Yellow Tinge | 203 | 711 | None | 7.93 | None | 0.92 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliftop House | 2023-10-16 | D2023-10-11 |  | <0.009 | Clear | 167 | 584 | None | 7.99 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2023-10-16 | D2023-10-12 |  | <0.009 | Clear | 182 | 615 | None | 7.99 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Senior Citizens Club | 2023-10-25 | D2023-10-13 |  | <0.009 | Clear | 200 | 643 | None | 8 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2023-10-25 | D2023-10-14 |  | <0.009 | Clear | 182 | 653 | None | 8.03 | None | 0.6 | <1 Not Detected | <1 Not Detected
Zone 3 - Hillside | 2023-10-25 | D2023-10-15 |  | <0.009 | Clear | 165 | 606 | None | 8.03 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-10-25 | D2023-10-16 |  | <0.009 | Clear | 170 | 587 | None | 8.02 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angle | 2023-11-08 | D2023-11-1 |  | <0.009 | Clear | 170 | 636 | None | 8.03 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Bus Stop | 2023-11-08 | D2023-11-2 |  | <0.009 | Clear | 171 | 635 | None | 8.13 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 3 - HighCliffe House | 2023-11-08 | D2023-11-3 |  | <0.009 | Clear | 168 | 622 | None | 8.04 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-11-08 | D2023-11-4 |  | <0.009 | Clear | 168 | 608 | None | 8.08 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Shop | 2023-11-15 | D2023-11-5 |  | <0.009 | Clear | 164 | 604 | None | 8.05 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2023-11-15 | D2023-11-6 |  | <0.009 | Clear | 168 | 637 | None | 7.9 | None | 0.46 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar Uni Halls | 2023-11-15 | D2023-11-7 |  | <0.009 | Clear | 164 | 618 | None | 8.01 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-11-15 | D2023-11-8 |  | <0.009 | Clear | 162 | 615 | None | 7.96 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Eddie Stores Laguna | 2023-11-22 | D2023-11-9 |  | <0.009 | Clear | 172 | 566 | None | 8 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 - Victoria Stadium Tennis | 2023-11-22 | D2023-11-10 |  | <0.009 | Clear | 161 | 608 | None | 8.17 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2023-11-22 | D2023-11-11 |  | <0.009 | Clear | 162 | 615 | None | 7.99 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-11-22 | D2023-11-12 |  | <0.009 | Clear | 164 | 608 | None | 7.99 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Small Boats Marina | 2023-11-29 | D2023-11-13 |  | <0.009 | Clear | 177 | 638 | None | 8.03 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2 - Midtown The Little Kitchen | 2023-11-29 | D2023-11-14 |  | <0.009 | Clear | 166 | 650 | None | 8.04 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 3 - HighCliffe House | 2023-11-29 | D2023-11-15 |  | <0.009 | Clear | 170 | 593 | None | 7.89 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2023-11-29 | D2023-11-16 |  | <0.009 | Clear | 159 | 608 | None | 7.92 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Charles Bruzon House | 2023-12-06 | D2023-12-1 |  | <0.009 | Clear | 186 | 652 | None | 7.92 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion LC | 2023-12-06 | D2023-12-2 |  | <0.009 | Clear | 174 | 629 | None | 8.13 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2023-12-06 | D2023-12-3 |  | <0.009 | Clear | 182 | 667 | None | 7.93 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovey's Cottage | 2023-12-06 | D2023-12-4 |  | <0.009 | Clear | 183 | 661 | None | 7.99 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Alemeda House | 2023-12-14 | D2023-12-5 |  | 0.026 | Clear | 186 | 670 | None | 7.85 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2 - John Mackintosh Hall | 2023-12-14 | D2023-12-6 |  | <0.009 | Clear | 176 | 664 | None | 7.79 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2023-12-14 | D2023-12-7 |  | <0.009 | Clear | 180 | 655 | None | 7.82 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2023-12-14 | D2023-12-8 |  | <0.009 | Clear | 183 | 672 | None | 7.84 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Carters | 2023-12-18 | D2023-12-9 |  | 0.026 | Clear | 175 | 653 | None | 7.99 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - Miss Shapes | 2023-12-18 | D2023-12-10 |  | <0.009 | Clear | 183 | 659 | None | 7.9 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2023-12-18 | D2023-12-11 |  | <0.009 | Clear | 173 | 661 | None | 7.88 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2023-12-18 | D2023-12-12 |  | <0.009 | Clear | 178 | 656 | None | 7.96 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 2 - Fit 4 Life City Mill lane | 2023-12-27 | D2023-12-13 |  | <0.009 | Clear | 175 | 659 | None | 8.11 | None | 0.36 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2023-12-27 | D2023-12-14 |  | <0.009 | Clear | 177 | 636 | None | 8.07 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2023-12-27 | D2023-12-15 |  | <0.009 | Clear | 170 | 635 | None | 7.96 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Waterport Plant Depot | 2024-01-02 | D2024-01-1 |  | <0.009 | Clear | 176 | 664 | None | 7.96 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 2 - The Ocean | 2024-01-02 | D2024-01-2 |  | <0.009 | Clear | 160 | 672 | None | 8.01 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Wembley Bar | 2024-01-02 | D2024-01-3 |  | <0.009 | Clear | 173 | 648 | None | 8.04 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-01-02 | D2024-01-4 |  | <0.009 | Clear | 161 | 639 | None | 7.98 | None | 0.37 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-01-10 | D2024-01-5 |  | <0.009 | Clear | 175 | 649 | None | 7.91 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2024-01-10 | D2024-01-6 |  | <0.009 | Clear | 160 | 652 | None | 7.85 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2024-01-10 | D2024-01-7 |  | <0.009 | Clear | 167 | 626 | None | 7.99 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-01-10 | D2024-01-8 |  | <0.009 | Clear | 168 | 634 | None | 7.92 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Cepsa | 2024-01-17 | D2024-01-9 |  | <0.009 | Clear | 165 | 620 | None | 7.88 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 - Bristol Hotel | 2024-01-17 | D2024-01-10 |  | <0.009 | Clear | 166 | 641 | None | 7.84 | None | 0.48 | <1 Not Detected | <1 Not Detected
Zone 3 - Mifix | 2024-01-17 | D2024-01-11 |  | <0.009 | Clear | 166 | 626 | None | 7.88 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2024-01-17 | D2024-01-12 |  | <0.009 | Clear | 163 | 630 | None | 7.92 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Gasa Meter Box | 2024-01-24 | D2024-01-13 |  | <0.009 | Clear | 182 | 641 | None | 7.88 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 2 - The Right Cut | 2024-01-24 | D2024-01-14 |  | <0.009 | Clear | 162 | 640 | None | 7.84 | None | 0.41 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House Meter Box | 2024-01-24 | D2024-01-15 |  | <0.009 | Clear | 156 | 608 | None | 7.88 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-01-24 | D2024-01-16 |  | <0.009 | Clear | 170 | 640 | None | 7.92 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - New Harbours | 2024-01-31 | D2024-01-17 |  | <0.009 | Clear | 181 | 686 | None | 8.09 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - Midtown | 2024-01-31 | D2024-01-18 |  | <0.009 | Clear | 183 | 688 | None | 8.08 | None | 0.38 | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2024-01-31 | D2024-01-19 |  | <0.009 | Clear | 206 | 755 | None | 8.09 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-01-31 | D2024-01-20 |  | <0.009 | Clear | 190 | 721 | None | 8.15 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - Hight Level - Leanse Place | 2024-02-07 | D2024-02-1 |  | <0.009 | Clear | 196 | 690 | None | 8.22 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2024-02-07 | D2024-02-2 |  | <0.009 | Clear | 186 | 703 | None | 8.09 | None | 0.8 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2024-02-07 | D2024-02-3 |  | <0.009 | Clear | 191 | 715 | None | 8.21 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-02-07 | D2024-02-4 |  | <0.009 | Clear | 197 | 732 | None | 8.15 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - North Mole, Flying Angel | 2024-02-13 | D2024-02-5 |  | 0.011 | Clear | 200 | 724 | None | 8.22 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 2 - Piazza drinking fountain | 2024-02-13 | D2024-02-6 |  | <0.009 | Clear | 179 | 756 | None | 7.98 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Ocean Views | 2024-02-13 | D2024-02-7 |  | 0.012 | Clear | 181 | 788 | None | 8.19 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-02-13 | D2024-02-8 |  | 0.012 | Clear | 173 | 733 | None | 8.04 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-02-21 | D2024-02-9 |  | <0.009 | Clear | 190 | 699 | None | 8.11 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 - Swift Dry Cleaners | 2024-02-21 | D2024-02-10 |  | <0.009 | Clear | 203 | 776 | None | 7.96 | None | 0.4 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-02-21 | D2024-02-11 |  | <0.009 | Clear | 183 | 681 | None | 8.11 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-02-21 | D2024-02-12 |  | <0.009 | Clear | 185 | 684 | None | 8.24 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Gib Oil (Laguna) | 2024-02-28 | D2024-02-13 |  | <0.009 | Clear | 190 | 684 | None | 7.85 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2024-02-28 | D2024-02-14 |  | <0.009 | Clear | 207 | 763 | None | 8.03 | None | 0.44 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe | 2024-02-28 | D2024-02-15 |  | <0.009 | Clear | 176 | 673 | None | 8.15 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2024-02-28 | D2024-02-16 |  | <0.009 | Clear | 184 | 813 | None | 8.14 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2024-03-06 | D2024-03-1 |  | <0.009 | Clear | 186 | 644 | None | 8.22 | None | 0.57 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2024-03-06 | D2024-03-2 |  | <0.009 | Clear | 206 | 791 | None | 7.99 | None | 0.42 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar Uni halls | 2024-03-06 | D2024-03-3 |  | <0.009 | Clear | 172 | 653 | None | 7.93 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2024-03-06 | D2024-03-4 |  | <0.009 | Clear | 175 | 642 | None | 7.89 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Custom's House | 2024-03-12 | D2024-03-5 |  | <0.009 | Clear | 171 | 670 | None | 8.21 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-03-12 | D2024-03-6 |  | <0.009 | Clear | 181 | 664 | None | 8.09 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mew's | 2024-03-12 | D2024-03-7 |  | <0.009 | Clear | 168 | 631 | None | 8.08 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2024-03-12 | D2024-03-8 |  | <0.009 | Clear | 166 | 618 | None | 8.03 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - New Harbours Lower Floor Toilets | 2024-03-25 | D2024-03-9 |  | <0.009 | Clear | 167 | 649 | None | 8.1 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-03-25 | D2024-03-10 |  | <0.009 | Clear | 189 | 778 | None | 8 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mew's | 2024-03-25 | D2024-03-11 |  | <0.009 | Clear | 164 | 661 | None | 8.05 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-03-25 | D2024-03-12 |  | <0.009 | Clear | 173 | 647 | None | 8.03 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Leanse Place | 2024-04-02 | D2024-04-1 |  | <0.009 | Clear | 194 | 730 | None | 8.04 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2024-04-02 | D2024-04-2 |  | <0.009 | Clear | 187 | 724 | None | 8.02 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-04-04 | D2024-04-3 |  | <0.009 | Clear | 183 | 692 | None | 8.06 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-04-02 | D2024-04-4 |  | <0.009 | Clear | 182 | 675 | None | 8.07 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-04-09 | D2024-04-5 |  | <0.009 | Clear | 179 | 682 | None | 8.22 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 2 - City Mill Lane | 2024-04-09 | D2024-04-6 |  | <0.009 | Clear | 181 | 737 | None | 8.18 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-04-09 | D2024-04-7 |  | <0.009 | Clear | 180 | 698 | None | 8.18 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-04-09 | D2024-04-8 |  | <0.009 | Clear | 188 | 691 | None | 8.16 | None | 0.45 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Waterport Plant Depot | 2024-04-16 | D2024-04-9 |  | <0.009 | Clear | 192 | 697 | None | 8.31 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 2 - Governor's Parade | 2024-04-16 | D2024-04-10 |  | <0.009 | Clear | 197 | 718 | None | 8.21 | None | 0.334 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-04-16 | D2024-04-11 |  | <0.009 | Clear | 186 | 688 | None | 8.28 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-04-16 | D2024-04-12 |  | <0.009 | Clear | 182 | 699 | None | 8.18 | None | 0.09 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Cepsa Airport | 2024-04-24 | D2024-04-13 |  | <0.009 | Clear | 190 | 735 | None | 7.99 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 2 - Vinopolis | 2024-04-24 | D2024-04-14 |  | <0.009 | Clear | 195 | 754 | None | 7.96 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe | 2024-04-24 | D2024-04-15 |  | <0.009 | Clear | 160 | 611 | None | 8.03 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2024-04-24 | D2024-04-16 |  | <0.009 | Clear | 165 | 629 | None | 8.12 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Hospital | 2024-05-03 | D2024-05-1 |  | <0.009 | Clear | 187 | 662 | None | 7.95 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2024-05-03 | D2024-05-2 |  | <0.009 | Clear | 222 | 846 | None | 8.24 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-05-03 | D2024-05-3 |  | <0.009 | Clear | 154 | 637 | None | 7.98 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-05-03 | D2024-05-4 |  | <0.009 | Clear | 166 | 645 | None | 7.88 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Schomberg | 2024-05-08 | D2024-05-5 |  | <0.009 | Clear | 184 | 638 | None | 7.69 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - 4 Library Gardens | 2024-05-08 | D2024-05-6 |  | <0.009 | Clear | 218 | 770 | None | 7.74 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa View Terraces | 2024-05-08 | D2024-05-7 |  | <0.009 | Clear | 168 | 657 | None | 7.91 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-05-08 | D2024-05-8 |  | <0.009 | Clear | 173 | 649 | None | 7.87 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Cruise Terminal Toilets | 2024-05-13 | D2024-05-9 |  | <0.009 | Clear | 175 | 694 | None | 7.24 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 2 - Governor's Parade | 2024-05-13 | D2024-05-10 |  | <0.009 | Clear | 194 | 76 | None | 7.65 | None | 0.44 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar Uni | 2024-05-13 | D2024-05-11 |  | <0.009 | Clear | 176 | 696 | None | 7.85 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-05-13 | D2024-05-12 |  | <0.009 | Clear | 176 | 679 | None | 7.88 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Prior Park | 2024-05-22 | D2024-05-13 |  | <0.009 | Clear | 197 | 717 | None | 7.71 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 - Midtown | 2024-05-22 | D2024-05-14 |  | <0.009 | Clear | 196 | 757 | None | 7.82 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2024-05-22 | D2024-05-15 |  | <0.009 | Clear | 196 | 658 | None | 7.81 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2024-05-22 | D2024-05-16 |  | <0.009 | Clear | 169 | 665 | None | 7.82 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-05-31 | D2024-05-17 |  | <0.009 | Clear | 174 | 692 | None | 8 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - City Mill Lane | 2024-05-28 | D2024-05-18 |  | <0.009 | Clear | 194 | 717 | None | 8.27 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-05-28 | D2024-05-19 |  | <0.009 | Clear | 176 | 667 | None | 8.23 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-05-28 | D2024-05-20 |  | <0.009 | Clear | 179 | 652 | None | 8.23 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - 25/6 South Barrack Road | 2024-06-05 | D2024-06-1 |  | <0.009 | Clear | 191 | 732 | None | 7.77 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-06-05 | D2024-06-2 |  | <0.009 | Clear | 195 | 780 | None | 7.69 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Hillside | 2024-06-05 | D2024-06-3 |  | <0.009 | Clear | 191 | 717 | None | 7.88 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2024-06-05 | D2024-06-4 |  | <0.009 | Clear | 190 | 723 | None | 7.9 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2024-06-12 | D2024-06-5 |  | <0.009 | Clear | 198 | 754 | None | 7.44 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion | 2024-06-12 | D2024-06-6 |  | <0.009 | Clear | 204 | 808 | None | 7.92 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mew's | 2024-06-12 | D2024-06-7 |  | <0.009 | Clear | 180 | 715 | None | 7.8 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-06-12 | D2024-06-8 |  | <0.009 | Clear | 189 | 707 | None | 7.8 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Victoria Stadium (Airport) | 2024-06-18 | D2024-06-9 |  | <0.009 | Clear | 180 | 704 | None | 7.94 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Toilets | 2024-06-20 | D2024-06-10 |  | <0.009 | Clear | 197 | 769 | None | 7.85 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2024-06-18 | D2024-06-11 |  | <0.009 | Clear | 178 | 691 | None | 7.94 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-06-18 | D2024-06-12 |  | <0.009 | Clear | 180 | 694 | None | 7.94 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Victoria Stadium (Airport) | 2024-06-18 | D2024-06-13 |  | <0.009 | Clear | 180 | 704 | None | 7.94 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Toilets | 2024-06-20 | D2024-06-14 |  | <0.009 | Clear | 197 | 769 | None | 7.85 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2024-06-18 | D2024-06-15 |  | <0.009 | Clear | 178 | 691 | None | 7.94 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-06-18 | D2024-06-16 |  | <0.009 | Clear | 180 | 694 | None | 7.94 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Pig & Whistle | 2024-06-24 | D2024-06-17 |  | <0.009 | Clear | 189 | 791 | None | 7.93 | None | N/A | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Toilets | 2024-06-24 | D2024-06-18 |  | <0.009 | Clear | 197 | 782 | None | 8 | None | N/A | <1 Not Detected | <1 Not Detected
Zone 3 - Bistro Point | 2024-06-24 | D2024-06-19 |  | <0.009 | Clear | 173 | 675 | None | 7.87 | None | N/A | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-06-24 | D2024-06-20 |  | <0.009 | Clear | 188 | 695 | None | 7.85 | None | N/A | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Waterport Plant Depot | 2024-07-03 | D2024-07-1 |  | <0.009 | Clear | 181 | 722 | None | 7.7 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - 94/3 Irish Town | 2024-07-03 | D2024-07-2 |  | <0.009 | Clear | 201 | 807 | None | 7.65 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliftons | 2024-07-03 | D2024-07-3 |  | <0.009 | Clear | 170 | 683 | None | 7.7 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-07-03 | D2024-07-4 |  | <0.009 | Clear | 173 | 687 | None | 7.71 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Carters | 2024-07-10 | D2024-07-5 |  | <0.009 | Clear | 151 | 648 | None | 7.83 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 2 - Midtown | 2024-07-10 | D2024-07-6 |  | <0.009 | Clear | 211 | 785 | None | 7.79 | None | 0.37 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe | 2024-07-10 | D2024-07-7 |  | <0.009 | Clear | 173 | 682 | None | 7.84 | None | 0.42 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2024-07-10 | D2024-07-8 |  | <0.009 | Clear | 169 | 689 | None | 7.85 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-07-15 | D2024-07-9 |  | <0.009 | Clear | 173 | 680 | None | 7.69 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2024-07-15 | D2024-07-10 |  | <0.009 | Clear | 194 | 759 | None | 7.68 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-07-15 | D2024-07-11 |  | <0.009 | Clear | 167 | 662 | None | 7.69 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den | 2024-07-15 | D2024-07-12 |  | <0.009 | Clear | 173 | 696 | None | 7.82 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Alemeda Gardens Toilet | 2024-07-24 | D2024-07-13 |  | <0.009 | Clear | 177 | 718 | None | 7.97 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-07-24 | D2024-07-14 |  | <0.009 | Clear | 197 | 746 | None | 7.96 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-07-24 | D2024-07-15 |  | <0.009 | Clear | 187 | 724 | None | 8.1 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-07-24 | D2024-07-16 |  | <0.009 | Clear | 190 | 736 | None | 7.96 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2024-08-14 | D2024-08-1 |  | <0.009 | Clear | 186 | 726 | None | 8.22 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 2 - Latinos | 2024-08-14 | D2024-08-2 |  | <0.009 | Clear | 194 | 746 | None | 7.96 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University | 2024-08-14 | D2024-08-3 |  | <0.009 | Clear | 196 | 738 | None | 8.1 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-08-14 | D2024-08-4 |  | <0.009 | Clear | 194 | 737 | None | 8.06 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Morrisons | 2024-08-21 | D2024-08-5 |  | <0.009 | Clear | 193 | 743 | None | 7.9 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - Bristol Hotel | 2024-08-21 | D2024-08-6 |  | <0.009 | Clear | 196 | 766 | None | 7.89 | None | 0.6 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2024-08-21 | D2024-08-7 |  | <0.009 | Clear | 219 | 796 | None | 8.05 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-08-21 | D2024-08-8 |  | <0.009 | Clear | 203 | 785 | None | 8.07 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Catalan Bay Toilets | 2024-08-29 | D2024-08-9 |  | <0.009 | Clear | 225 | 791 | None | 8.21 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion | 2024-08-29 | D2024-08-10 |  | <0.009 | Clear | 218 | 799 | None | 8 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Hillside | 2024-08-29 | D2024-08-11 |  | <0.009 | Clear | 223 | 889 | None | 8.24 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-08-29 | D2024-08-12 |  | <0.009 | Clear | 224 | 849 | None | 8.24 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Senior Citizen's Club | 2024-09-04 | D2024-09-1 |  | <0.009 | Clear | 204 | 840 | None | 7.98 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 - Midtown | 2024-09-04 | D2024-09-2 |  | <0.009 | Clear | 207 | 800 | None | 8.04 | None | 0.31 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mew's | 2024-09-04 | D2024-09-3 |  | <0.009 | Clear | 232 | 843 | None | 8.2 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2024-09-04 | D2024-09-4 |  | <0.009 | Clear | 232 | 844 | None | 8.23 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2024-09-11 | D2024-09-5 |  | <0.009 | Clear | 193 | 721 | None | 8.21 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2024-09-11 | D2024-09-6 |  | <0.009 | Clear | 211 | 813 | None | 8.05 | None | 0.65 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-09-11 | D2024-09-7 |  | <0.009 | Clear | 183 | 737 | None | 8.2 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2024-09-12 | D2024-09-8 |  | <0.009 | Clear | 187 | 708 | None | 8.12 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-09-19 | D2024-09-9 |  | <0.009 | Clear | 202 | 757 | None | 8.11 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham Toilets | 2024-09-19 | D2024-09-10 |  | <0.009 | Clear | 214 | 782 | None | 8.02 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-09-19 | D2024-09-11 |  | <0.009 | Clear | 206 | 774 | None | 8 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den | 2024-09-19 | D2024-09-12 |  | <0.009 | Clear | 204 | 766 | None | 8.11 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Alemeda Gardens Toilet | 2024-09-25 | D2024-09-13 |  | <0.009 | Clear | 204 | 773 | None | 8.03 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-09-25 | D2024-09-14 |  | <0.009 | Clear | 214 | 800 | None | 8.08 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University | 2024-09-25 | D2024-09-15 |  | <0.009 | Clear | 203 | 786 | None | 8.15 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-09-25 | D2024-09-16 |  | <0.009 | Clear | 200 | 738 | None | 8.19 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2024-10-02 | D2024-10-1 |  | <0.009 | Clear | 181 | 742 | None | 8.25 | None | 0.49 | <1 Not Detected | <1 Not Detected
Zone 2 - City Mill Lane - Fit 4 Life | 2024-10-02 | D2024-10-2 |  | <0.009 | Clear | 196 | 784 | None | 8.18 | None | 0.69 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2024-10-02 | D2024-10-3 |  | <0.009 | Clear | 192 | 734 | None | 8.1 | None | 0.72 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-10-02 | D2024-10-4 |  | <0.009 | Clear | 201 | 792 | None | 8.08 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Gib Oil Marine | 2024-10-08 | D2024-10-5 |  | <0.009 | Clear | 163 | 662 | None | 8.06 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Toilets | 2024-10-08 | D2024-10-6 |  | <0.009 | Clear | 205 | 773 | None | 8 | None | 0.42 | <1 Not Detected | <1 Not Detected
Zone 3 - Clifftop House | 2024-10-08 | D2024-10-7 |  | <0.009 | Clear | 170 | 678 | None | 8.05 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-10-08 | D2024-10-8 |  | <0.009 | Clear | 171 | 689 | None | 8.04 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Victoria Stadium (Cepsa) | 2024-10-16 | D2024-10-9 |  | <0.009 | Clear | 150 | 662 | None | 7.99 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion | 2024-10-16 | D2024-10-10 |  | <0.009 | Clear | 163 | 738 | None | 8.07 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 3 - HIllside | 2024-10-16 | D2024-10-11 |  | <0.009 | Clear | 173 | 663 | None | 8.04 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2024-10-16 | D2024-10-12 |  | <0.009 | Clear | 158 | 661 | None | 8.04 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Unite Office | 2024-10-21 | D2024-10-13 |  | <0.009 | Clear | 175 | 729 | None | 7.92 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2024-10-21 | D2024-10-14 |  | <0.009 | Clear | 181 | 720 | None | 7.96 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-10-21 | D2024-10-15 |  | <0.009 | Clear | 177 | 688 | None | 7.98 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2024-10-21 | D2024-10-16 |  | <0.009 | Clear | 170 | 684 | None | 7.98 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-10-31 | D2024-10-17 |  | <0.009 | Clear | 174 | 646 | None | 8.23 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2024-10-31 | D2024-10-18 |  | <0.009 | Clear | 176 | 673 | None | 8.15 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-10-31 | D2024-10-19 |  | <0.009 | Clear | 160 | 652 | None | 8.11 | None | 0.59 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2024-10-31 | D2024-10-20 |  | <0.009 | Clear | 177 | 647 | None | 8.08 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Cumberland Terraces | 2024-11-06 | D2024-11-1 |  | <0.009 | Clear | 185 | 671 | None | 7.75 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-11-06 | D2024-11-2 |  | <0.009 | Clear | 178 | 697 | None | 8.01 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Halls | 2024-11-06 | D2024-11-3 |  | <0.009 | Clear | 164 | 669 | None | 8.12 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-11-06 | D2024-11-4 |  | <0.009 | Clear | 172 | 650 | None | 8.05 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2024-11-14 | D2024-11-5 |  | <0.009 | Clear | 172 | 678 | None | 8.16 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 2 - Cheers - Cornwall centre | 2024-11-14 | D2024-11-6 |  | <0.009 | Clear | 184 | 691 | None | 8 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2024-11-14 | D2024-11-7 |  | <0.009 | Clear | 180 | 689 | None | 8.09 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2024-11-14 | D2024-11-8 |  | <0.009 | Clear | 175 | 724 | None | 8.11 | None | 0.71 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Custom's House | 2024-11-20 | D2024-11-9 |  | <0.009 | Clear | 160 | 689 | None | 8.1 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Toilets | 2024-11-20 | D2024-11-10 |  | <0.009 | Clear | 183 | 699 | None | 8.05 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliffside | 2024-11-20 | D2024-11-11 |  | <0.009 | Clear | 171 | 683 | None | 8.08 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries | 2024-11-20 | D2024-11-12 |  | <0.009 | Clear | 181 | 685 | None | 8.05 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Cemetery | 2024-11-27 | D2024-11-13 |  | <0.009 | Clear | 160 | 688 | None | 8.1 | None | 0.29 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion | 2024-11-27 | D2024-11-14 |  | <0.009 | Clear | 216 | 720 | None | 8.21 | None | 0.32 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mew's | 2024-11-27 | D2024-11-15 |  | <0.009 | Clear | 169 | 683 | None | 8.16 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2024-11-27 | D2024-11-16 |  | <0.009 | Clear | 183 | 688 | None | 8.1 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Rock on the Rock | 2024-12-04 | D2024-12-1 |  | <0.009 | Clear | 179 | 713 | None | 8.07 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2024-12-04 | D2024-12-2 |  | <0.009 | Clear | 184 | 708 | None | 7.98 | None | 0.41 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2024-12-04 | D2024-12-3 |  | <0.009 | Clear | 185 | 692 | None | 8.2 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den | 2024-12-04 | D2024-12-4 |  | <0.009 | Clear | 179 | 681 | None | 8.17 | None | 0.39 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Moorish Castle Estate Shop | 2024-12-11 | D2024-12-5 |  | <0.009 | Clear | 181 | 656 | None | 8.12 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2024-12-11 | D2024-12-6 |  | <0.009 | Clear | 182 | 708 | None | 8.06 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2024-12-11 | D2024-12-7 |  | <0.009 | Clear | 170 | 647 | None | 8.16 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2024-12-11 | D2024-12-8 |  | <0.009 | Clear | 170 | 642 | None | 8.15 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Alemeda Gardens Toilet | 2024-12-18 | D2024-12-9 |  | <0.009 | Clear | 184 | 660 | None | 7.98 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2024-12-18 | D2024-12-10 |  | <0.009 | Clear | 180 | 703 | None | 8.03 | None | 0.41 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Toilets | 2024-12-18 | D2024-12-11 |  | <0.009 | Clear | 188 | 662 | None | 8.08 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2024-12-18 | D2024-12-12 |  | <0.009 | Clear | 184 | 656 | None | 8.46 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2025-01-02 | D2025-01-01 |  | <0.009 | Clear | 182 | 637 | None | 8.38 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 2 - Bristol Hotel | 2025-01-02 | D2025-01-02 |  | <0.009 | Clear | 192 | 629 | None | 8.11 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2025-01-02 | D2025-01-03 |  | <0.009 | Clear | 170 | 640 | None | 8.08 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2025-01-02 | D2025-01-04 |  | <0.009 | Clear | 172 | 645 | None | 8.09 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Morrisons | 2025-01-08 | D2025-01-05 |  | <0.009 | Clear | 150 | 609 | None | 7.92 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2025-01-08 | D2025-01-06 |  | <0.009 | Clear | 172 | 698 | None | 8.03 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Hillside | 2025-01-08 | D2025-01-07 |  | <0.009 | Clear | 184 | 660 | None | 8.08 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries Toilet | 2025-01-08 | D2025-01-08 |  | <0.009 | Clear | 200 | 648 | None | 8.1 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Forbes | 2025-01-15 | D2025-01-09 |  | <0.009 | Clear | 146 | 586 | None | 8.04 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion | 2025-01-15 | D2025-01-10 |  | <0.009 | Clear | 180 | 697 | None | 8.08 | None | 0.51 | <1 Not Detected | <1 Not Detected
Zone 3 - Special Olympics Sports Complex | 2025-01-15 | D2025-01-11 |  | <0.009 | Clear | 164 | 668 | None | 8.17 | None | 0.73 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2025-01-15 | D2025-01-12 |  | <0.009 | Clear | 158 | 629 | None | 8.02 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - New Harbours | 2025-01-21 | D2025-01-13 |  | <0.009 | Clear | 174 | 611 | None | 8.01 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 2 - John Macintosh Hall | 2025-01-21 | D2025-01-14 |  | <0.009 | Clear | 182 | 700 | None | 8.06 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Point Toilets | 2025-01-21 | D2025-01-15 |  | <0.009 | Clear | 176 | 617 | None | 8.08 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2025-01-21 | D2025-01-16 |  | <0.009 | Clear | 174 | 620 | None | 7.98 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Olindo Shop | 2025-01-29 | D2025-01-17 |  | <0.009 | Clear | 144 | 693 | None | 8.02 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 2 - Domino's Pizza | 2025-01-29 | D2025-01-18 |  | <0.009 | Clear | 182 | 736 | None | 7.92 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Highcliffe House | 2025-01-29 | D2025-01-19 |  | <0.009 | Clear | 154 | 642 | None | 8.01 | None | 0.33 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2025-01-29 | D2025-01-20 |  | <0.009 | Clear | 172 | 664 | None | 8.01 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Leanse Plane | 2025-02-05 | D2025-02-01 |  | <0.009 | Clear | 156 | 622 | None | 7.64 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2025-02-05 | D2025-02-02 |  | <0.009 | Clear | 204 | 756 | None | 7.78 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Toilets | 2025-02-05 | D2025-02-03 |  | <0.009 | Clear | 170 | 661 | None | 7.91 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den | 2025-02-05 | D2025-02-04 |  | <0.009 | Clear | 164 | 649 | None | 7.95 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Leanse Plane | 2025-02-13 | D2025-02-05 |  | <0.009 | Clear | 178 | 618 | None | 8.12 | None | 0.54 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2025-02-13 | D2025-02-06 |  | <0.009 | Clear | 194 | 674 | None | 8.33 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Toilets | 2025-02-13 | D2025-02-07 |  | <0.009 | Clear | 170 | 627 | None | 8.06 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den | 2025-02-13 | D2025-02-08 |  | <0.009 | Clear | 168 | 619 | None | 8.15 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Pig and Whistle | 2025-04-03 | D2025-04-01 |  | <0.009 | Clear | 156 | 622 | None | 7.89 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - Gib Oil | 2025-04-03 | D2025-04-02 |  | <0.009 | Clear | 194 | 703 | None | 7.68 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2025-04-03 | D2025-04-03 |  | <0.009 | Clear | 142 | 625 | None | 8.01 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries Toilet | 2025-04-03 | D2025-04-04 |  | <0.009 | Clear | 148 | 614 | None | 7.96 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Victoria Stadium (cepsa) | 2025-04-09 | D2025-04-05 |  | <0.009 | Clear | 128 | 619 | None | 7.91 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion (Line wall Road Toilet) | 2025-04-09 | D2025-04-06 |  | <0.009 | Clear | 182 | 692 | None | 7.99 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Cliffside | 2025-04-09 | D2025-04-07 |  | <0.009 | Clear | 176 | 604 | None | 7.97 | None | 0.3 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2025-04-09 | D2025-04-08 |  | <0.009 | Clear | 160 | 583 | None | 7.93 | None | 0.25 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Eroski | 2025-04-14 | D2025-04-09 |  | <0.009 | Clear | 170 | 579 | None | 8.08 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - The Little Kitchen (Midtown) | 2025-04-14 | D2025-04-10 |  | <0.009 | Clear | 180 | 575 | None | 7.99 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Halls | 2025-04-14 | D2025-04-11 |  | <0.009 | Clear | 168 | 594 | None | 8.02 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2025-04-14 | D2025-04-12 |  | <0.009 | Clear | 170 | 591 | None | 8.03 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Olindo Shop | 2025-04-22 | D2025-04-13 |  | <0.009 | Clear | 166 | 760 | None | 8 | None | 0.141 | <1 Not Detected | <1 Not Detected
Zone 2 - Piazza Toilets | 2025-04-22 | D2025-04-14 |  | <0.009 | Clear | 184 | 721 | None | 7.92 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa Mew's | 2025-04-24 | D2025-04-15 |  | <0.009 | Clear |  | 560 | None | 8.1 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2025-04-22 | D2025-04-16 |  | <0.009 | Clear | 202 | 834 | None | 7.88 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 1 - High level - Carter's Shop | 2025-04-29 | D2025-04-17 |  | <0.009 | Clear | 164 | 589 | None | 8.32 | None | 0.66 | <1 Not Detected | <1 Not Detected
Zone 2 - ICC | 2025-04-29 | D2025-04-18 |  | <0.009 | Clear | 182 | 661 | None | 8.04 | None | 0.2 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Toilets | 2025-04-29 | D2025-04-19 |  | <0.009 | Clear | 156 | 571 | None | 8.12 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries Toilet | 2025-04-29 | D2025-04-20 |  | <0.009 | Clear | 170 | 584 | None | 8.02 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - North Mole Security Post | 2025-05-07 | D2025-05-01 |  | <0.009 | Clear | 146 | 618 | None | 8.11 | None | 0.27 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham | 2025-05-07 | D2025-05-02 |  | <0.009 | Clear | 181 | 689 | None | 7.97 | None | 0.67 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2025-05-07 | D2025-05-03 |  | <0.009 | Clear | 178 | 694 | None | 8.02 | None | 0.54 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2025-05-07 | D2025-05-04 |  | <0.009 | Clear | 175 | 664 | None | 8 | None | 0.35 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - North Mole Security Post | 2025-05-14 | D2025-05-05 |  | <0.009 | Clear | 139 | 663 | None | 8.12 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham | 2025-05-14 | D2025-05-06 |  | <0.009 | Clear | 166 | 670 | None | 7.88 | None | 0.64 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2025-05-14 | D2025-05-07 |  | <0.009 | Clear | 169 | 693 | None | 8.01 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 4 - Devil's Gap | 2025-05-14 | D2025-05-08 |  | <0.009 | Clear | 183 | 711 | None | 8 | None | 0.08 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - AquaGib Stores | 2025-05-22 | D2025-05-09 |  | <0.009 | Clear | 165 | 679 | None | 8.13 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 2 - Pick Wicks Bisto | 2025-05-22 | D2025-05-10 |  | <0.009 | Clear | 168 | 724 | None | 7.93 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Special Olympics Sports Complex | 2025-05-22 | D2025-05-11 |  | <0.009 | Clear | 185 | 732 | None | 8.05 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2025-05-22 | D2025-05-12 |  | <0.009 | Clear | 184 | 715 | None | 8.02 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Cumberland | 2025-06-04 | D2025-06-01 |  | <0.009 | Clear | 193 | 740 | None | 7.85 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 2 - Casemates Toilets | 2025-06-04 | D2025-06-02 |  | <0.009 | Clear | 191 | 749 | None | 7.91 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa point sports complex kitchen | 2025-06-04 | D2025-06-03 |  | <0.009 | Clear | 188 | 738 | None | 8.04 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 4 - Tovery's Cottage | 2025-06-04 | D2025-06-04 |  | <0.009 | Clear | 187 | 710 | None | 8.03 | None | 0.11 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Olindo Shop | 2025-06-09 | D2025-06-05 |  | <0.009 | Clear | 190 | 768 | None | 7.87 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 2 - King's Bastion | 2025-06-09 | D2025-06-06 |  | <0.009 | Clear | 193 | 750 | None | 7.98 | None | 0.46 | <1 Not Detected | <1 Not Detected
Zone 3 - Lathbury Sports Complex | 2025-06-09 | D2025-06-07 |  | <0.009 | Clear | 210 | 809 | None | 8.09 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2025-06-09 | D2025-06-08 |  | <0.009 | Clear | 207 | 824 | None | 8.09 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1 - High Level - Leanse Plane | 2025-06-19 | D2025-06-09 |  | <0.009 | Clear | 193 | 700 | None | 7.84 | None | 0.13 | <1 Not Detected | <1 Not Detected
Zone 2 - Emilio Youth Hostel | 2025-06-19 | D2025-06-10 |  | <0.009 | Clear | 199 | 748 | None | 7.87 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Toilets | 2025-06-19 | D2025-06-11 |  | <0.009 | Clear | 192 | 739 | None | 8.06 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 4 - Upper Galleries Toilet | 2025-06-19 | D2025-06-12 |  | <0.009 | Clear | 184 | 745 | None | 8.07 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 1 - Shipping - Flying Angel | 2025-07-02 | D2025-07-01 |  | <0.009 | Clear | 185 | 690 | None | 8.12 | None | 0.22 | <1 Not Detected | <1 Not Detected
Zone 2 - Grand Battery House | 2025-07-02 | D2025-07-02 |  | <0.009 | Clear | 200 | 719 | None | 8.17 | None | 0.5 | <1 Not Detected | <1 Not Detected
Zone 3 - Bleak House | 2025-07-02 | D2025-07-03 |  | <0.009 | Clear | 180 | 689 | None | 8.2 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 4 - Bruce's Farm | 2025-07-02 | D2025-07-04 |  | <0.009 | Clear | 188 | 701 | None | 8.19 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 1 - Westside - Hustle and Flow | 2025-07-09 | D2025-07-05 |  | <0.009 | Clear | 201 | 753 | None | 8.57 | None | 0.15 | <1 Not Detected | <1 Not Detected
Zone 2 - Vinopolis | 2025-07-09 | D2025-07-06 |  | <0.009 | Clear | 204 | 780 | None | 7.89 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Edward's House | 2025-07-09 | D2025-07-07 |  | <0.009 | Clear | 170 | 706 | None | 8.02 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Ape's Den | 2025-07-09 | D2025-07-08 |  | <0.009 | Clear | 173 | 767 | None | 8.02 | None | 0.14 | <1 Not Detected | <1 Not Detected
Zone 1 - North Front - Caleta Toilet (Seawave) | 2025-07-16 | D2025-07-09 |  | <0.009 | Clear | 188 | 709 | None | 8.15 | None | 0.24 | <1 Not Detected | <1 Not Detected
Zone 2 - Piece of Cake | 2025-07-16 | D2025-07-10 |  | <0.009 | Clear | 197 | 778 | None | 8 | None | 0.26 | <1 Not Detected | <1 Not Detected
Zone 3 - Brympton | 2025-07-16 | D2025-07-11 |  | <0.009 | Clear | 189 | 734 | None | 8.2 | None | 0.21 | <1 Not Detected | <1 Not Detected
Zone 4 - Hay's Level Tunnel | 2025-07-16 | D2025-07-12 |  | <0.009 | Clear | 192 | 732 | None | 8.15 | None | 0.23 | <1 Not Detected | <1 Not Detected
Zone 1 - South District - Alameda express | 2025-07-23 | D2025-07-13 |  | <0.009 | Clear | 192 | 731 | None | 7.77 | None | 0.34 | <1 Not Detected | <1 Not Detected
Zone 2 - Chatham | 2025-07-23 | D2025-07-14 |  | <0.009 | Clear | 204 | 781 | None | 7.74 | None | 0.28 | <1 Not Detected | <1 Not Detected
Zone 3 - Europa point toilets | 2025-07-23 | D2025-07-15 |  | <0.009 | Clear | 178 | 668 | None | 7.83 | None | 0.18 | <1 Not Detected | <1 Not Detected
Zone 4 - Poca Roca | 2025-07-23 | D2025-07-16 |  | <0.009 | Clear | 186 | 702 | None | 7.84 | None | 0.19 | <1 Not Detected | <1 Not Detected
Zone 1 - Moorish Castle Estate - Olindo Shop | 2025-07-30 | D2025-07-17 |  | <0.009 | Clear | 180 | 691 | None | 7.93 | None | 0.12 | <1 Not Detected | <1 Not Detected
Zone 2 - Piazza Toilets | 2025-07-30 | D2025-07-18 |  | <0.009 | Clear | 184 | 764 | None | 7.85 | None | 0.16 | <1 Not Detected | <1 Not Detected
Zone 3 - Lathbury Sports Complex | 2025-07-30 | D2025-07-19 |  | <0.009 | Clear | 157 | 677 | None | 7.9 | None | 0.17 | <1 Not Detected | <1 Not Detected
Zone 4 - Moorish Castle Tourist Site | 2025-07-30 | D2025-07-20 |  | <0.009 | Clear | 194 | 760 | None | 7.97 | None | 0.1 | <1 Not Detected | <1 Not Detected
Zone 3 - Gibraltar University Toilets | 45776
Zone 4 - Upper Galleries Toilet | 45776
Zone 1 - Shipping - North Mole Security Post | 45784
Zone 2 - Chatham | 45784
Zone 3 - Bleak House | 45784
Zone 4 - Devil's Gap | 45784
Zone 1 - Shipping - North Mole Security Post | 45791
Zone 2 - Chatham | 45791
Zone 3 - Bleak House | 45791
Zone 4 - Devil's Gap | 45791
Zone 1 - North Front - AquaGib Stores | 45799
Zone 2 - Pick Wicks Bisto | 45799
Zone 3 - Special Olympics Sports Complex | 45799
Zone 4 - Hay's Level Tunnel | 45799
Zone 1 - South District - Cumberland | 45812
Zone 2 - Casemates Toilets | 45812
Zone 3 - Europa point sports complex kitchen | 45812
Zone 4 - Tovery's Cottage | 45812
Zone 1 - Moorish Castle Estate - Olindo Shop | 45817
Zone 2 - King's Bastion | 45817
Zone 3 - Lathbury Sports Complex | 45817
Zone 4 - Moorish Castle Tourist Site | 45817
Zone 1 - High Level - Leanse Plane | 45827
Zone 2 - Emilio Youth Hostel | 45827
Zone 3 - Gibraltar University Toilets | 45827
Zone 4 - Upper Galleries Toilet | 45827
Zone 1 - Shipping - Flying Angel | 45840
Zone 2 - Grand Battery House | 45840
Zone 3 - Bleak House | 45840
Zone 4 - Bruce's Farm | 45840
Zone 1 - Westside - Hustle and Flow | 45847
Zone 2 - Vinopolis | 45847
Zone 3 - Edward's House | 45847
Zone 4 - Ape's Den | 45847
Zone 1 - North Front - Caleta Toilet (Seawave) | 45854
Zone 2 - Piece of Cake | 45854
Zone 3 - Brympton | 45854
Zone 4 - Hay's Level Tunnel | 45854
Zone 1 - South District - Alameda express | 45861
Zone 2 - Chatham | 45861
Zone 3 - Europa point toilets | 45861
Zone 4 - Poca Roca | 45861
Zone 1 - Moorish Castle Estate - Olindo Shop | 45868
Zone 2 - Piazza Toilets | 45868
Zone 3 - Lathbury Sports Complex | 45868
Zone 4 - Moorish Castle Tourist Site | 45868

## Audit Monitoring Results
Potable Water Mains Supply - Audit Monitoring Analytical Results
Samples from the potable water distribution network are collected by AquaGib quarterly and are analysed at an independent labroatary.
Standards are in accordance with the Public Health Water Rules 1994, which incoporate the requirements set by the European Directive of Drinking Water 98/83/EC
Note 1: Acceptable to consumers and no abnormal change
Sample Location | Date of Collection of Sample | Analysis Reference Number | Audit Lab Reference Number | Parameter | 1,2-Dichloroethane | Aluminium | Ammonium | Antimony | Arsenic | Benzene | Benzo(a)pyrene | Boron | Bromate | Cadmium | Chloride | Chromium | Colour | Conductivity | Copper | Cyanide | Epichlorohydrin | Fluoride | Iron | Lead | Manganese | Mercury | Nickel | Nitrate | Nitrite | Odour | Oxidisability | Pesticides- Total | pH | Polycyclic Aromatic Hydrocarbons (PAH)Total | Selenium | Sodium | Sulphate | Taste | Tetrachloroethene | Trichloroethene | Trihalomethanes Total | Turbidity | Vinyl Chloride | Coliform Bacteria | E.coli | Entereococci
|  |  |  | Units | μg/l | μg/l Al | mg/l NH4 | μg/l Sb | μg/l As | μg/l | μg/l | mg/l B | μg/l BrO3 | μg/l Cd | mg/l Cl | μg/l Cr | mg/l Pt/Co | μS/cm | mg/l Cu | μg/l CN | μg/l | mg/l F | μg/l Fe | μg/l Pb | μg/l Mn | μg/l Hg | μg/l Ni | mg/l NO3 | mg/l NO2 | Qualitative | mg/l O2 | μg/l | pH units | μg/l | μg/l Se | mg/l Na | mg/l SO4 | Qualitative | μg/l | μg/l | μg/l | NTU | μg/l | number/100ml | number/100ml | number/100ml
|  |  |  | Standard | 3 | 200 | 0.5 | 5 | 10 | 1 | 0.01 | 1 | 10 | 5 | 250 | 50 | Note 1 | 2500 | 2 | 50 | 0.1 | 1.5 | 200 | 10 | 50 | 1 | 20 | 50 | 0.5 | Note 1 | 5 | 0.5 | ≥ 6.5, ≤ 9.5 | 0.1 | 10 | 200 | 250 | Note 1 | Combined Standard of 10 |  | 100 | Note 1 | 0.5 | 0 | 0 | 0
Zone1, North Front, Both Worlds | 2009-04-14 | 2009/Q2/1 | 968734 |  | <0.049 | <2.9 | <0.019 | 0.38 | 0.45 | <0.030 | <0.00062 | 0.47 | 2.7 | <0.0081 | 190 | <0.20 | 11 | 650 | 0.0037 | <0.66 | <0.10 | <0.027 | <2.3 | 1.1 | 0.49 | <0.037 | 0.83 | <0.78 | <0.0014 | 0 | 0.6 | 0 | 7.71 | 0.00091 | 0.32 | 67 | 2.2 | 0 | <0.16 | <0.26 | 1.7 | 0.049 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3, Europa District, Sunset Close | 2009-04-14 | 2009/Q2/2 | 968735 |  | <0.049 | <2.9 | <0.019 | <0.28 | 0.66 | <0.030 | <0.00062 | 0.54 | <0.95 | <0.0081 | 180 | <0.20 | <0.93 | 600 | 0.0045 | <0.66 | <0.1 | <0.027 | 150 | 0.6 | 2.2 | <0.037 | 2.4 | 1.2 | <0.0014 | 0 | 0.4 | 0 | 8.26 | 0.0044 | 0.43 | 60 | 1.9 | 0 | <0.16 | <0.26 | 2.4 | 0.44 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Education Department Queensway | 2009-07-21 | 2009/Q3/1 | 988662 |  | <0.049 | <2.9 | <0.019 | <0.28 | 0.35 | <0.030 | <0.00062 | 0.49 | <0.95 | <0.0081 | 150 | <0.20 | <0.93 | 530 | 0.00093 | <0.66 | <0.1 | <0.027 | 18 | 0.2 | 0.6 | <0.037 | 1.3 | 1.4 | <0.0014 | 0 | 1.9 | 0 | 7.91 | 0.0022 | <0.31 | 53 | 1.9 | 0 | <0.16 | <0.26 | 9.5 | 0.093 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply, Bleak House,Elliots Battery | 2009-07-21 | 2009/Q3/2 | 988663 |  | <0.049 | 12 | 0.059 | <0.28 | 0.71 | <0.030 | 0.0012 | 0.74 | <0.95 | <0.0081 | 220 | <0.20 | <0.93 | 690 | 0.0066 | <0.66 | <0.1 | <0.027 | 430 | 0.52 | 11 | <0.037 | 2.7 | 1.2 | <0.0014 | 0 | 0.59 | 0 | 7.93 | 0.01238 | <0.31 | 75 | 1.2 | 0 | 0 | <0.26 | 2.4 | 1.5 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,Shipping District,Port Department | 2009-10-12 | 2009/Q4/1 | 1006065 |  | <0.049 | 6.4 | <0.019 | 0.33 | 0.6 | <0.030 | <0.00062 | 0.29 | 6.5 | <0.0081 | 220 | <0.20 | <0.93 | 730 | <0.00064 | <0.66 | <0.1 | <0.027 | <2.3 | 0.073 | 0.5 | <0.037 | 0.78 | 1.2 | <0.0014 | 0 | 0.69 | 0 | 7.63 | 0.003 | 0.36 | 79 | 2.4 | 0 | 0 | <0.26 | 0 | 0.19 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,The Cliftons | 2009-10-12 | 2009/Q4/2 | 1006066 |  | <0.049 | <2.9 | <0.019 | <0.28 | 0.71 | <0.030 | <0.00062 | 0.59 | <0.97 | <0.0081 | 190 | 0.26 | 3.2 | 630 | <0.00064 | <0.66 | <0.5 | <0.027 | 6.5 | 0.33 | 0.57 | <0.037 | 0.79 | 1.1 | <0.0014 | 0 | 0.26 | 0 | 8.27 | 0.0018 | <0.31 | 68 | 1.5 | 0 | <0.16 | <0.26 | 7.2 | 0.055 | <0.10 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply, Buena Vista Road | 2009-12-24 | 2009/Q4/3 | 1018757 |  | <0.049 | <2.9 | <0.019 | <0.28 | 0.54 | <0.030 | <0.00062 | 0.51 | <0.97 | <0.0081 | 180 | <0.20 | <0.93 | 570 | 0.0018 | <0.30 | <0.1 | <0.027 | 49 | 0.28 | 1.1 | <0.037 | 2 | 1 | <0.0014 | 0 | 0.29 | 0 | 8.36 | 0 | 0.35 | 62 | 3.4 | 0 | <0.16 | <0.26 | 0 | 0.15 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,St Marys School | 2009-12-24 | 2009/Q4/4 | 1018766 |  | <0.049 | <2.9 | <0.019 | <0.28 | 0.76 | <0.030 | <0.00062 | 0.66 | <0.97 | <0.0081 | 200 | 0.27 | 1.2 | 670 | <0.00064 | <0.66 | <0.5 | <0.027 | <2.3 | 0.94 | 0.54 | <0.037 | 0.17 | 1.1 | <0.0014 | 0 | 0.45 | 0 | 8.19 | 0.00254 | 0.44 | 74 | 1.8 | 0 | <0.16 | <0.26 | 1.9 | 0.051 | <0.10 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,High Level,Sacred Heart Middle School | 2010-03-18 | 2010/Q1/1 | 1034370 |  | <0.049 | <2.9 | <0.019 | <0.28 | 1.8 | <0.030 | <0.00062 | 0.59 | <0.97 | <0.0081 | 600 | 0.26 | <0.93 | 1900 | <0.00064 | <0.30 | <0.1 | 0.036 | 8.7 | 0.19 | 1.2 | <0.037 | 1.7 | 1.2 | <0.0014 | 0 | 0.16 | 0 | 8.15 | 0 | 2.1 | 300 | 71 | 0 | <0.16 | <0.26 | 17.5 | 0.14 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Lathbury Industrial Park | 2010-03-18 | 2010/Q1/2 | 1034371 |  | <0.049 | <7.3 | <0.019 | <0.28 | 0.64 | <0.030 | <0.00053 | 0.59 | <0.97 | <0.0081 | 180 | <0.20 | <0.93 | 620 | 0.0022 | <0.30 | <0.1 | <0.027 | 8.3 | 0.13 | 0.15 | <0.037 | 1.4 | 1 | <0.0014 | 0 | 0.26 | 0 | 7.95 | 0 | 0.51 | 72 | 2 | 0 | <0.16 | <0.26 | 1.3 | 0.11 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Catalan Bay Village | 2010-07-21 | 2010/Q3/1 | 1056059 & 1058732 |  | <0.049 | <7.3 | <0.019 | <0.28 | 0.7 | <0.030 | <0.00053 | 0.59 | <0.97 | <0.0082 | 190 | <0.20 | <0.93 | 630 | 0.00082 | <0.30 | <0.1 | <0.027 | 2.8 | 0.13 | 0.082 | <0.037 | 0.54 | 0.8 | <0.0014 | 0 | 0.38 | 0 | 8.15 | 0 | 0.59 | 74 | 1.8 | 0 | <0.16 | <0.26 | 0.92 | 0.16 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply,Elliots Battery Europa Flats | 2010-07-21 | 2010/Q3/2 | 1058733 & 1056058 |  | <0.049 | <7.3 | <0.019 | <0.28 | 0.63 | <0.030 | <0.00053 | 0.72 | 6.3 | <0.0081 | 210 | <0.20 | <0.93 | 670 | 0.007 | <0.30 | <0.10 | <0.027 | 96 | 0.92 | 1.6 | <0.037 | 2.4 | <0.78 | <0.0014 | 0 | 0.33 | 0.0063 | 8.15 | 0 | 0.43 | 79 | 1.8 | 0 | <0.16 | <0.26 | 1.6 | 0.43 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Sunset Close | 2010-10-18 | 2010/Q4/1 | 1074376 |  | <0.049 | <7.3 | <0.019 | <0.28 | 1.7 | <0.030 | <0.00053 | 0.61 | <0.97 | 0.0084 | 190 | <0.20 | <0.93 | 630 | 0.0084 | 0.39 | <0.10 | 0.03 | 270 | 0.95 | 2.1 | <0.037 | 2.6 | <0.78 | <0.0014 | 0 | <0.092 | 0 | 8.03 | 0 | 1.3 | 69 | 1.2 | 0 | <0.16 | <0.26 | 2.6 | 0.36 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,North Front,Devils Tower Road | 2010-10-18 | 2010/Q4/2 | 1074377 |  | <0.049 | <7.3 | <0.019 | <0.28 | 0.46 | <0.030 | <0.00053 | 0.86 | <0.97 | 0.029 | 220 | <0.20 | <0.93 | 740 | 0.0011 | 1.4 | <0.10 | <0.027 | 15 | 0.74 | 0.26 | <0.037 | 2.3 | <0.78 | <0.0014 | 0 | 0.27 | 0.0064 | 7.84 | 0 | <0.31 | 89 | 1.3 | 0 | <0.16 | <0.26 | 4.39 | 0.14 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply,HM Customs,Land Frontier | 2010-12-07 | 2010/Q4/3 | 1084519 |  | <0.049 | <7.3 | 0.021 | <0.28 | 0.52 | <0.030 | <0.00061 | 0.7 | <0.97 | <0.0081 | 200 | <0.20 | <0.93 | 650 | 0.0013 | 0.5 | <0.10 | 0.006 | 36 | 0.075 | 0.1 | <0.037 | 1.4 | <0.17 | <0.0029 | 0 | 0.26 | 0 | 8.11 | 0 | <0.31 | 74 | 1.9 | 0 | <0.16 | <0.26 | 0.84 | 0.32 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Education Department Queensway | 2010-12-07 | 2010/Q4/4 | 1084520 |  | <0.049 | <7.3 | <0.019 | <0.28 | 1.6 | <0.030 | <0.00053 | 0.82 | 4.5 | 0.011 | 230 | <0.20 | <0.93 | 770 | 0.0059 | 0.33 | <0.10 | 0.04 | 30 | 0.57 | 0.43 | <0.037 | 1.6 | <0.78 | <0.0014 | 0 | 0.34 | 0 | 7.91 | 0 | 1.3 | 88 | 1.2 | 0 | <0.16 | <0.26 | 4 | 0.19 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,West Side Reclamation,Morrison Supermarket | 2011-03-22 | 2011/Q1/1 | 59803 |  | <0.049 | <7.3 | 0.021 | <0.28 | 0.48 | <0.030 | <0.00061 | 0.72 | <0.97 | <0.0081 | 220 | <0.20 | <0.93 | 700 | <0.00064 | <0.30 | <0.10 | 0.003 | <2.6 | 0.48 | <0.060 | <0.037 | 0.42 | <0.17 | <0.0029 | 0 | 0.19 | 0 | 8.21 | 0 | <0.31 | 85 | 3.1 | 0 | <0.16 | <0.26 | 0.88 | 0.16 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,High Cliffs | 2011-03-22 | 2011/Q1/2 | 59809 |  | <0.036 | <7.3 | <0.0072 | <0.28 | 0.54 | <0.014 | <0.00053 | 0.59 | <0.97 | <0.0081 | 200 | <0.20 | 1.1 | 660 | 0.0009 | <0.30 | <0.10 | <0.027 | 20 | 6.1 | 0.18 | <0.037 | 0.45 | <1.7 | <0.0029 | 0 | 0.31 | 0 | 8.24 | 0 | <0.31 | 76 | 4 | 0 | <0.051 | <0.044 | 1.6 | 0.068 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply,Elliots Battery Europa Flats | 2011-06-07 | 2011/Q2/1 | 105808 |  | <0.036 | <7.3 | <0.0072 | <0.28 | 0.4 | <0.014 | <0.00053 | 0.9 | <0.30 | <0.0081 | 210 | <0.20 | <0.93 | 700 | 0.0056 | 0.43 | <0.10 | <0.027 | 470 | 3 | 6.4 | <0.037 | 1.2 | <1.7 | <0.0029 | 0 | 0.36 | 0 | 8 | 0 | <0.31 | 95 | 4.2 | 0 | <0.051 | <0.044 | 1.8 | 0.95 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Central Police Station | 2011-06-07 | 2011/Q2/2 | 105810 |  | <0.036 | <7.3 | <0.0072 | <0.28 | 0.46 | <0.014 | <0.00053 | 0.57 | <0.97 | <0.0081 | 200 | <0.20 | 1.4 | 660 | 0.0021 | <0.30 | <0.10 | <0.027 | 10 | 1.6 | <0.060 | <0.037 | 0.4 | <1.7 | <0.0029 | 0 | 0.25 | 0 | 8.21 | 0.00053 | <0.31 | 77 | 3.9 | 0 | <0.051 | <0.044 | 1.6 | 0.15 | 0.5 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply,Buena Vista Hostel | 2011-08-02 | 2011/Q3/1 | 139231 |  | <0.060 | <6.6 | <0.0072 | <0.28 | 0.58 | <0.013 | <0.00053 | 0.65 | 1.5 | <0.0081 | 180 | <0.20 | <0.93 | 650 | <0.00064 | 0.33 | <0.10 | <0.024 | 11 | 0.17 | 0.36 | <0.037 | 0.1 | <1.7 | <0.0029 | 0 | 0.54 | 0 | 8.45 | 0 | <0.31 | 80 | 3.7 | 0 | <0.12 | <0.098 | 8.17 | 0.082 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,St Mary's School | 2011-08-02 | 2011/Q3/2 | 139233 |  | <0.036 | <7.3 | <0.0072 | <0.28 | 0.37 | <0.014 | <0.00053 | 0.81 | <0.30 | <0.0081 | 220 | <0.20 | <0.93 | 720 | 0.0027 | <3.0 | <0.10 | <0.027 | <2.6 | <0.025 | <0.060 | <0.037 | <0.034 | <1.7 | <0.0029 | 0 | 0.42 | 0 | 8.37 | 0 | <0.31 | 88 | 4.6 | 0 | <0.051 | <0.044 | 1.7 | 0.077 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Sunset Close | 2011-12-13 | 2011/Q4/1 | 225673 |  | <0.025 | <6.6 | <0.0072 | <0.033 | 0.2 | <0.013 | <0.00056 | 0.75 | <0.30 | <0.0024 | 210 | 0.099 | <0.93 | 710 | 0.033 | <0.30 | <0.10 | <0.024 | 320 | 0.68 | 1.7 | <0.013 | 0.69 | <1.7 | <0.0029 | 0 | 0.1 | 0.0187 | 8.21 | 0 | 0.21 | 92 | 5.8 | 0 | <0.12 | <0.098 | N/A | 0.84 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,North Front,Both Worlds | 2011-12-13 | 2011/Q4/1 | 225672 |  | <0.060 | <6.6 | <0.0072 | <0.28 | 0.6 | <0.013 | <0.00053 | 0.66 | 9 | <0.0091 | 200 | <0.20 | <0.93 | 710 | 0.0042 | <0.30 | <0.10 | <0.024 | 15 | 0.45 | 0.29 | <0.037 | 0.83 | <1.7 | <0.0029 | 0 | 0.54 | 0.04 | 8.05 | 0 | <0.31 | 80 | 2.2 | 0 | <0.12 | <0.098 | 9.97 | 0.098 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,High Cliffs | 2012-03-21 | 2012/Q1/1 | 284501 |  | <0.025 | <6.6 | 0.026 | <0.033 | 0.151 | <0.013 | <0.00056 | N/A | <0.30 | <0.0024 | 210 | <0.025 | <0.93 | 710 | <0.00093 | <0.30 | <0.10 | 0.11 | 27 | 0.065 | 0.39 | <0.013 | 0.13 | <1.7 | <0.0029 | 0 | 0.093 | 0 | 8.24 | 0 | <0.078 | 90 | 6.8 | 0 | <0.12 | <0.098 | 1.4 | 0.092 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,High Level,Willis's Parade | 2012-03-21 | 2012/Q1/2 | 284502 |  | <0.025 | <6.6 | <0.0072 | <0.033 | 0.15 | 0.015 | <0.00056 | 0.57 | <0.30 | <0.0024 | 200 | 0.1 | <0.93 | 690 | <0.00093 | <0.30 | <0.10 | <0.024 | 5.7 | 0.18 | 0.22 | <0.013 | 0.17 | <1.7 | <0.0029 | 0 | 0.22 | 0.0187 | 8.29 | 0 | 0.19 | 88 | 7.9 | 0 | <0.12 | <0.098 | N/A | 0.12 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Gibraltar Museum | 2012-07-30 | 2012/Q3/1 | 367341 |  | <0.025 | <6.6 | 0.016 | <0.033 | <0.045 | <0.013 | <0.00056 | 0.71 | <0.30 | 0.0063 | 220 | <0.025 | <0.93 | 730 | 0.0021 | <0.30 | <0.10 | 0.1 | 6.1 | <0.014 | 0.48 | <0.013 | <0.020 | <1.7 | <0.0029 | 0 | 0.25 | 0 | 8.33 | 0 | <0.078 | 98 | 7.3 | 0 | <0.12 | <0.098 | 6 | 0.056 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
M.O.D Supply,Europa Path, Naval Hospital | 2012-07-30 | 2012/Q3/2 | 367343 |  | <0.025 | 12 | <0.0072 | <0.033 | 0.068 | 0.16 | <0.00056 | 0.68 | <0.30 | 0.025 | 200 | 0.044 | <0.93 | 680 | 0.0025 | 0.44 | <0.10 | 0.041 | 21 | 0.46 | 0.75 | <0.013 | 0.65 | <1.7 | <0.0029 | 0 | 0.51 | 0.0488 | 8.05 | 0 | <0.078 | 81 | 3.5 | 0 | <0.12 | <0.098 | 1.21 | 0.19 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,South District,Rosia Dale | 2012-10-29 | 2012/Q4/1 | 429081 |  | <0.025 | 6.6 | 0.0079 | <0.033 | 0.057 | <0.013 | <0.00056 | 0.8 | <0.30 | 0.0085 | 210 | 0.12 | <0.93 | 700 | 0.0016 | 0.45 | <0.10 | 0.045 | 22 | 0.19 | <0.18 | <0.013 | 0.5 | <1.7 | <0.0029 | 0 | 0.19 | 0.0488 | 8.27 | 0 | <0.078 | 87 | 3.6 | 0 | <0.12 | <0.098 | 1.34 | 0.12 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Lancester House | 2012-10-29 | 2012/Q4/2 | 429087 |  | <0.025 | <6.6 | <0.0072 | <0.033 | <0.045 | <0.013 | <0.00058 | 0.91 | <0.30 | 0.015 | 190 | <0.025 | <0.93 | 650 | 0.018 | 0.31 | <0.10 | 0.052 | 130 | 0.46 | 2.1 | <0.013 | 0.66 | <1.7 | <0.0029 | 0 | <0.090 | 0.0624 | 8.12 | 0.0004 | <0.078 | 81 | 3.6 | 0 | <0.12 | <0.098 | 6.73 | 0.22 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,Waterport District | 2013-02-12 | 2013/Q1/1 | 494094 |  | <0.025 | <6.6 | <0.0072 | <0.033 | <0.045 | <0.013 | <0.00056 | 0.88 | 1.2 | 0.021 | 240 | <0.025 | <0.93 | 780 | 0.065 | <0.30 | <0.10 | 0.05 | 17 | 0.14 | 0.22 | <0.013 | 0.33 | <1.7 | <0.0029 | 0 | <0.090 | 0.039 | 7.76 | 0 | <0.078 | 91 | 2 | 0 | <0.12 | <0.098 | 1.2 | 0.052 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District | 2013-02-12 | 2013/Q1/2 | 494106 |  | <0.025 | <6.6 | 0.015 | 0.044 | 0.12 | <0.013 | <0.00056 | 0.82 | 1.5 | 0.023 | 200 | <0.025 | 3.1 | 670 | 0.0071 | <0.30 | <0.10 | 0.045 | 110 | 0.53 | 1.4 | <0.013 | 0.59 | <1.7 | <0.0029 | 0 | 0.19 | 0 | 8.18 | 0.00095 | <0.078 | 82 | 3.8 | 0 | <0.12 | <0.098 | 4.08 | 0.4 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,Shipping District,Waterport Gib Oil | 2013-07-01 | 2013/Q3/1 | 579584 |  | <0.025 | <6.6 | 0.013 | <0.033 | 0.093 | <0.013 | <0.00056 | 0.6 | <0.30 | <0.0024 | 190 | 0.14 | 4 | 640 | <0.00093 | <0.30 | <0.10 | 0.042 | <1.2 | 0.051 | <0.18 | <0.013 | 0.11 | <1.7 | <0.0029 | 0 | <0.092 | 0.013 | 8.25 | 0 | <0.078 | 68 | 1.4 | 0 | <0.12 | <0.098 | 2.77 | 0.074 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Brymton Estate,Victoria Tower | 2013-07-01 | 2013/Q3/2 | 579585 |  | <0.025 | 8.5 | <0.0072 | <0.333 | 0.1 | <0.013 | <0.00056 | 0.69 | 0.94 | 0.0068 | 200 | 0.071 | <0.93 | 690 | 0.0017 | <0.30 | <0.10 | 0.04 | 65 | 0.51 | 1.6 | <0.013 | 0.42 | <1.7 | <0.0029 | 0 | 0.56 | 0 | 8.16 | 0 | <0.078 | 90 | 5.1 | 0 | <0.12 | <0.098 | 6.9 | 0.25 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Moorish Castle,Low Level,20 Line Wall Road | 2013-08-05 | 2013/Q3/3 | 602928 |  | <0.025 | <6.6 | 0.018 | 0.061 | 0.059 | <0.016 | <0.00056 | 0.54 | <0.30 | 0.0045 | 230 | 0.038 | <0.93 | 790 | <0.00093 | <0.30 | <0.10 | 0.044 | <1.2 | <0.014 | <0.18 | <0.013 | 0.074 | 2.2 | <0.0029 | 0 | 0.47 | 0.017 | 8.24 | 0.00058 | <0.078 | 110 | 11 | 0 | <0.12 | <0.098 | 3.51 | 0.04 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Tourist Site,100 Ton Gun | 2013-08-05 | 2013/Q3/4 | 602929 |  | <0.025 | 20 | 0.0089 | <0.033 | 0.077 | <0.013 | <0.00056 | 0.61 | 1.6 | 0.015 | 210 | 0.053 | <0.93 | 690 | 0.0047 | <0.30 | <0.10 | 0.037 | 58 | 0.42 | 0.94 | <0.013 | 1 | <1.7 | <0.0029 | 0 | 0.54 | 0.31 | 8.27 | 0 | <0.078 | 82 | 5 | 0 | <0.12 | <0.098 | 5 | 0.18 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,ICC | 2013-10-16 | 2013/Q4/1 | 648736 |  | <0.025 | <6.6 | 0.0082 | <0.033 | 0.098 | <0.013 | <0.00056 | 0.71 | 20 | 0.0092 | 230 | 0.087 | <0.93 | 750 | 0.025 | <0.30 | <0.10 | 0.033 | 25 | 0.24 | 0.38 | 0.028 | 0.15 | <1.7 | <0.0029 | 0 | 0.48 | 0.0048 | 7.99 | 0 | 0.16 | 84 | 1.4 | 0 | <0.12 | <0.098 | 6.1 | 0.093 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Eliotts Battery | 2013-10-16 | 2013/Q4/2 | 648737 |  | <0.025 | 27 | 0.013 | <0.033 | <0.045 | <0.013 | <0.00056 | <0.0034 | 0.66 | 0.0079 | 210 | 0.1 | <0.93 | 720 | 0.0015 | <0.30 | <0.10 | 0.03 | 18 | 0.2 | 0.27 | <0.013 | 0.32 | <1.7 | <0.0029 | 0 | 0.66 | 0.026 | 7.78 | 0 | <0.078 | 94 | 5.7 | 0 | <0.12 | <0.098 | 5.6 | 0.077 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,North Front,Caleta Palace Hotel | 2013-11-18 | 2013/Q4/3 | 671867 |  | <0.025 | <6.6 | 0.016 | <0.033 | <0.045 | <0.013 | <0.00056 | 0.57 | <0.30 | <0.0024 | 210 | <0.025 | <0.93 | 720 | <0.00093 | <0.30 | <0.10 | 0.03 | <1.2 | 0.15 | <0.18 | <0.013 | 0.088 | <1.7 | <0.0029 | 0 | 0.28 | 0.0198 | 7.87 | 0 | <0.078 | 92 | 5.3 | 0 | <0.12 | <0.098 | 7.9 | 0.047 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,The Clifftons | 2013-11-18 | 2013/Q4/4 | 671871 |  | <0.025 | <6.6 | <0.0072 | 0.038 | 0.14 | <0.013 | <0.00056 | 0.75 | <0.30 | <0.0074 | 200 | 0.069 | <0.93 | 670 | 0.0046 | <0.30 | <0.10 | 0.029 | 0 | 0.83 | 3.8 | <0.013 | 0.79 | <1.7 | <0.0029 | 114 | 0.41 | 0.0092 | 8.11 | 0 | <0.078 | 0 | 6.3 | 0 | <0.12 | <0.098 | 6.84 | 0.17 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Sunset Close | 2014-02-03 | 2014/Q1/1 | 717996 |  | <0.025 | <6.6 | <0.0072 | <0.033 | 0.092 | <0.013 | <0.00056 | 0.52 | <0.30 | <0.0024 | 190 | <0.025 | <0.93 | 660 | 0.0011 | <0.30 | <0.10 | 0.027 | 0 | 0.048 | <0.18 | <0.013 | 1.3 | <1.7 | <0.0029 | 0 | 0.16 | 0 | 8.4 | 0 | <0.078 | 0 | 6.5 | 0 | <0.12 | <0.098 | 2.5 | 0.056 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,High Level,Sacred Heart Middle School | 2014-02-17 | 2014/Q1/2 | 723977 |  | <0.025 | 65 | 0.012 | <0.033 | 0.081 | <0.013 | <0.00056 | 0.77 | 10 | <0.0074 | 240 | 0.26 | <0.93 | 790 | 0.0033 | 0.43 | <0.10 | 0.027 | 0 | 0.66 | 0.69 | <0.013 | 0.93 | <1.7 | <0.0029 | 0 | 0.28 | 0 | 7.92 | 0 | <0.078 | 0 | 5.9 | 0 | <0.12 | <0.098 | 11.6 | 0.082 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Mini Market, 325 Main Street | 2014-04-07 | 2014/Q2/1 | 753704 |  | <0.025 | <6.6 | 0.0086 | <0.033 | 0.09 | 0.013 | <0.00056 | 0.5 | <0.30 | <0.0024 | 190 | <0.025 | <0.93 | 650 | <0.00093 | <0.30 | <0.10 | 0.034 | 0 | <0.014 | <0.18 | <0.013 | <0.020 | <1.7 | <0.0029 | 0 | <0.092 | 0 | 8.29 | 0 | <0.078 | 0 | 6.8 | 0 | <0.12 | <0.098 | 0.9 | 0.046 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Buena Vista Estate | 2014-04-07 | 2014/Q2/2 | 753705 |  | <0.025 | <6.6 | 0.0087 | <0.033 | <0.045 | <0.013 | <0.00056 | 0.53 | <0.30 | 0.0027 | 190 | 0.054 | <0.93 | 700 | <0.00093 | <0.30 | <0.10 | 0.02 | 9.5 | 0.073 | <0.18 | <0.013 | 0.26 | <1.7 | <0.0029 | 0 | <0.092 | 0.0039 | 8.11 | 0.00102 | <0.078 | 87 | 5.3 | 0 | 0.24 | <0.098 | 7.71 | 0.075 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,South District,Vineyard Estate | 2014-07-14 | 2014/Q3/1 | 813768 |  | <0.025 | 8.8 | 0.0073 | <0.033 | <0.045 | <0.013 | <0.00056 | 0.62 | 6.8 | 0.0096 | 230 | 0.048 | <0.93 | 770 | 0.0031 | <0.30 | <0.10 | 0.03 | 39 | 0.26 | 0.35 | <0.013 | 0.2 | <1.7 | <0.0029 | 0 | <0.092 | 0.023 | 7.78 | 0.00109 | <0.078 | 77 | 5.1 | 0 | 0.24 | 0.13 | 8.22 | 0.18 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,The High Cliffs | 2014-07-14 | 2014/Q3/2 | 813769 |  | <0.025 | <6.6 | <0.0072 | <0.033 | 0.09 | <0.013 | <0.00056 | 0.66 | <0.30 | 0.0057 | 200 | <0.025 | <0.93 | 720 | 0.0019 | <0.30 | <0.10 | <0.024 | 11 | 0.2 | <0.18 | <0.013 | <0.020 | <1.7 | <0.0029 | 0 | 0.41 | 0 | 8.13 | 0 | <0.078 | 97 | 6.6 | 0 | 0.3 | <0.098 | 7.2 | 0.082 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Europa Point Public Toilets | 2014-10-27 | 2014/Q4/1 | 881900 |  | <0.025 | <6.6 | 0.022 | <0.033 | 0.071 | <0.013 | <0.00056 | 0.68 | <0.30 | 0.0046 | 210 | 0.2 | <0.93 | 720 | 0.015 | <0.30 | <0.10 | <0.024 | 73 | 1.2 | 3.5 | <0.013 | 1.4 | <1.7 | <0.0029 | 0 | 0.38 | 0.038 | 8.15 | 0 | <0.078 | 100 | 5.7 | 0 | <0.12 | <0.098 | 6 | 0.58 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,ICC | 2014-10-27 | 2014/Q4/2 | 882466 |  | <0.025 | <6.6 | <0.0072 | <0.033 | 0.13 | 0.022 | <0.00056 | 0.62 | <0.30 | <0.0024 | 200 | <0.025 | <0.93 | 710 | 0.0013 | <0.30 | <0.10 | <0.024 | <1.2 | 0.18 | <0.18 | <0.013 | <0.020 | <1.7 | <0.0029 | 0 | 0.47 | 0.0057 | 8.19 | 0 | <0.078 | 98 | 6.8 | 0 | 0.3 | 0.2 | 3.6 | 0.054 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Elliots battery | 2015-01-12 | 2015/Q1/1 | 929477 |  | <0.025 | <6.6 | <0.0072 | <0.033 | 0.069 | <0.013 | <0.00056 | 0.58 | <0.30 | <0.0024 | 200 | <0.025 | <0.93 | 680 | <0.00093 | <0.30 | <0.10 | <0.024 | 3.6 | 0.051 | <0.18 | <0.013 | 0.087 | <1.7 | <0.0029 | 0 | 0.61 | 0 | 8.15 | 0 | <0.078 | 96 | 4.4 | 0 | <0.12 | <0.098 | 2.9 | 0.068 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,West Side District,Harbour Views | 2015-01-12 | 2015/Q1/2 | 930472 |  | <0.025 | <6.6 | 0.016 | <0.033 | 0.053 | <0.013 | <0.00056 | 0.59 | <0.30 | 0.0042 | 210 | <0.025 | <0.93 | 730 | 0.0015 | <0.30 | <0.10 | <0.024 | 2.8 | 0.11 | 0.23 | <0.013 | 0.22 | <1.7 | <0.0029 | 0 | 0.31 | 0 | 8.14 | 0 | <0.078 | 100 | 5.7 | 0 | <0.12 | <0.098 | 7 | 0.099 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Bleak House | 2015-05-12 | 2015/Q2/1 | 1001266 |  | <0.025 | <6.6 | 0.0099 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.57 | <0.30 | <0.017 | 200 | <0.044 | <0.93 | 730 | 0.0037 | <1.7 | <0.10 | <0.024 | 33 | 0.25 | 0.62 | <0.055 | 0.35 | <1.7 | <0.0029 | 0 | 0.31 | 0 | 8.17 | 0 | <0.16 | 100 | 6.3 | 0 | <0.12 | <0.098 | 5.17 | 0.19 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Mcintosh Hall,Main Street | 2015-05-12 | 2015/Q2/2 | 1001271 |  | <0.025 | <6.6 | 0.0078 | <0.033 | 0.072 | <0.013 | <0.00056 | 0.55 | <0.30 | <0.0024 | 190 | <0.025 | <0.93 | 640 | <0.00093 | <0.30 | <0.10 | <0.024 | <1.2 | 0.29 | <0.18 | <0.013 | 0.22 | <1.7 | <0.0029 | 0 | 0.73 | 0 | 8.17 | 0 | <0.078 | 37 | 3.5 | 0 | <0.12 | <0.098 | 1.6 | 0.063 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,North Front District,Both worlds | 2015-07-21 | 2015/Q3/1 | 1041819 |  | <0.025 | <6.6 | 0.011 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.58 | <0.30 | <0.017 | 210 | <0.044 | <0.93 | 760 | <0.0011 | <1.7 | <0.10 | <0.024 | 1.7 | 1.5 | <0.18 | <0.055 | 0.039 | <1.7 | <0.0029 | Slight Chlorine | <0.092 | 0 | 8.19 | 0 | <0.16 | 110 | 6.7 | 0 | <0.12 | <0.098 | 3.06 | 0.073 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Elliots battery | 2015-07-21 | 2015/Q3/2 | 1041821 |  | <0.025 | <6.6 | 0.0092 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.59 | 14 | <0.017 | 210 | <0.044 | <0.93 | 720 | 0.0016 | <1.7 | <0.10 | <0.024 | 13 | 0.16 | 0.28 | <0.055 | 0.19 | <1.7 | <0.0029 | 0 | 0.44 | 0 | 8.07 | 0 | <0.16 | 82 | 3.9 | 0 | <0.12 | <0.098 | 11.5 | 0.07 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,O Callaghan Eliotts Hotel | 2015-11-04 | 2015/Q4/1 | 1106176 |  | <0.025 | 7 | <0.0072 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.86 | <0.30 | <0.017 | 200 | 0.12 | <0.93 | 730 | 0.0044 | <1.7 | <0.10 | 0.026 | 34 | 3.9 | 0.33 | <0.055 | 0.33 | <1.7 | <0.0029 | 0 | 0.62 | 0 | 8.15 | 0 | <0.16 | 100 | 6.9 | 0 | <0.12 | <0.098 | 7.8 | 0.17 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,100 Ton Gun Gibraltar Tourist Board | 2015-11-04 | 2015/Q4/2 | 1106177 |  | <0.025 | 9 | <0.0072 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.7 | <0.30 | <0.017 | 190 | 0.099 | <0.93 | 700 | <0.0011 | <1.7 | <0.10 | 0.026 | <1.2 | 1.4 | <0.18 | <0.055 | <0.034 | <1.7 | <0.0029 | 0 | 0.55 | 0 | 8.23 | 0 | <0.16 | 99 | 7.9 | 0 | 0.12 | <0.098 | 5 | 0.082 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,Waterport District,Aquagib Distiller Canteen | 2016-01-25 | 2016/Q1/1 | 1155178 |  | <0.024 | 12 | 0.012 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.71 | <0.60 | <0.017 | 200 | <0.044 | <0.93 | 700 | 0.0043 | <1.7 | <0.10 | <0.024 | 7.4 | 2.5 | <0.18 | <0.055 | 0.37 | <1.7 | <0.0029 | 0 | 0.56 | 0 | 8.19 | 0 | <0.16 | 92 | 2.7 | 0 | <0.12 | <0.12 | 1 | 0.83 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,100 Ton Gun Gibraltar Tourist Board | 2016-01-25 | 2016/Q1/2 | 1155180 |  | <0.024 | 19 | 0.0073 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.73 | <0.60 | 0.026 | 220 | <0.044 | <0.93 | 790 | 0.012 | <1.7 | <0.10 | <0.024 | 110 | 26 | 3.7 | <0.055 | 2.5 | <1.7 | <0.0029 | 0 | 0.44 | 0 | 8.18 | 0 | <0.16 | 110 | 4.3 | 0 | <0.12 | <0.12 | 0 | 0.17 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Upper Rock District,Poca Roca Mter Room | 2016-04-25 | 2016/Q2/1 | 1208668 |  | <0.024 | 9.5 | 0.012 | <0.33 | 0.17 | <0.013 | <0.00056 | 0.6 | <0.30 | <0.017 | 160 | <0.044 | <0.93 | 690 | <0.0011 | <1.7 | <0.10 | <0.024 | 10 | 0.35 | <0.18 | <0.055 | 0.19 | <1.7 | <0.0029 | 0 | 0.32 | 0.011 | 8.27 | 0 | <0.16 | 96 | 3.2 | 0 | <0.12 | <0.12 | 0 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Upper Rock, Retreat Centre | 2016-04-25 | 2016/Q2/2 | 1208686 |  | <0.024 | 7.6 | 0.012 | <0.33 | 0.18 | <0.013 | <0.00056 | 0.61 | <0.30 | <0.017 | 190 | <0.044 | <0.93 | 700 | <0.0011 | <1.7 | <0.10 | <0.024 | <1.2 | 0.26 | <0.18 | <0.055 | 0.15 | 2.5 | <0.0029 | 0 | 0.32 | 0.01 | 8.27 | 0 | <0.16 | 59 | 2.9 | 0 | <0.12 | <0.12 | 0 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,Cornwalls Shopping Centre | 2016-04-25 | 2016/Q2/3 | 1208687 |  | <0.024 | 11 | <0.0072 | <0.33 | <0.14 | <0.013 | <0.00056 | 0.72 | 7.5 | <0.017 | 220 | <0.044 | <0.93 | 750 | 0.0073 | <1.7 | <0.10 | <0.024 | 77 | 4.2 | 4.1 | <0.055 | 0.43 | <1.7 | <0.0029 | 0 | 0.31 | 0.0099 | 8.16 | 0 | <0.16 | 96 | 2.9 | 0 | <0.12 | <0.12 | 1.2 | 0.26 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1 High Level 24 Prince Edwards Road | 2016-08-23 | 2016/Q3/1 | 1278169 |  | <0.024 | 8.8 | <0.0072 | <0.080 | 0.027 | <0.013 | <0.00056 | 0.67 | <0.30 | 0.014 | 200 | <0.083 | <0.93 | 700 | 0.0014 | <1.7 | <0.10 | 0.026 | 4.8 | 0.92 | <0.18 | <0.011 | 0.34 | <1.7 | <0.0029 | 0 | 0.53 | 0.0164 | 8.21 | 0 | <0.42 | 95 | 3.7 | 0 | <0.12 | <0.12 | 1.4 | 0.088 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3 Europa District St Bernards Church | 2016-08-23 | 2016/Q3/2 | 1278170 |  | <0.024 | 7.3 | <0.0072 | <0.080 | 0.033 | <0.013 | <0.00056 | 0.67 | <0.30 | 0.015 | 200 | <0.083 | <0.93 | 730 | 0.0019 | <1.7 | <0.10 | 0.024 | <1.2 | 0.51 | <0.18 | <0.011 | 0.67 | <1.7 | <0.0029 | 0 | 0.53 | 0.0177 | 8.2 | 0 | <0.42 | 100 | 3.4 | 0 | <0.12 | <0.12 | 0.69 | 0.087 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level,329 Main Street | 2016-10-31 | 2016/Q4/1 | 1323591 |  | <0.024 | 12 | <0.0072 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.66 | 17 | <0.0090 | 200 | <0.083 | <0.93 | 780 | 0.0025 | <1.7 | <0.10 | 0.025 | 16 | 0.25 | <0.18 | <0.011 | 0.16 | <1.7 | <0.0029 | 0 | 0.53 | 0.0164 | 8.04 | 0 | <0.42 | 87 | 3.3 | 0 | <0.12 | <0.12 | 4.8 | 0.092 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Upper Rock District,Lower Bruce's Farm | 2016-10-31 | 2016/Q4/2 | 1323594 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.032 | <0.013 | <0.00056 | 0.72 | <0.30 | <0.0090 | 210 | <0.083 | <0.93 | 740 | 0.001 | <1.7 | <0.10 | <0.024 | <1.2 | 0.17 | <0.18 | <0.011 | 0.17 | <1.7 | <0.0029 | 0 | 0.19 | 0.0051 | 8.1 | 0 | <0.42 | 99 | 2.8 | 0 | <0.12 | <0.12 | 0.73 | 0.074 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Airport car park unit1,British Lines | 2016-10-31 | 2016/Q4/3 | 1323601 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.041 | <0.013 | <0.00056 | 0.67 | <0.30 | <0.0090 | 220 | <0.083 | <0.93 | 780 | 0.0007 | <1.7 | <0.10 | <0.024 | <1.2 | 0.52 | <0.18 | <0.011 | 0.078 | <1.7 | <0.0029 | 0 | 0.44 | 0.0038 | 8.2 | 0 | <0.42 | 100 | 3.2 | 0 | <0.12 | <0.12 | 0 | 0.078 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,South District,City Fire Brigade | 2017-01-16 | 2017/Q1/1 | 1368734 |  | <0.024 | 11 | <0.0072 | <0.080 | 0.052 | <0.013 | <0.00056 | 0.74 | <0.30 | <0.0090 | 210 | <0.083 | <0.93 | 740 | 0.0015 | <1.7 | <0.10 | <0.024 | 5.1 | 0.3 | <0.18 | <0.011 | 0.48 | <1.7 | <0.0029 | 0 | 0.51 | 0.0608 | 8.25 | 0 | <0.42 | 110 | 3.5 | 0 | <0.12 | <0.12 | 0 | 0.099 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3, Europa District, Sunsat Close | 2017-01-16 | 2017/Q1/2 | 1368735 |  | <0.024 | 9.6 | <0.0072 | <0.080 | 0.039 | <0.013 | <0.00056 | 0.73 | <0.30 | <0.0090 | 220 | <0.083 | <0.93 | 770 | <0.00070 | <1.7 | <0.10 | <0.024 | <1.2 | 0.24 | <0.18 | 0.012 | 0.037 | <1.7 | <0.0029 | 0 | 0.95 | 0.0069 | 8.17 | 0 | 0.44 | 120 | 4.8 | 0 | <0.12 | <0.12 | 0 | 0.082 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,Low Level District,Sasemates Square | 2017-05-22 | 2017/Q2/1 | 1446769 |  | <0.024 | 11 | <0.0072 | <0.080 | 0.058 | <0.013 | <0.00056 | 0.77 | 12 | <0.0090 | 210 | <0.083 | <0.93 | 700 | 0.0028 | <1.7 | <0.10 | <0.024 | 82 | 0.53 | 0.66 | <0.011 | 0.69 | <1.7 | <0.0029 | 0 | <0.17 | 0.0453 | 7.84 | 0 | <0.42 | 88 | 0.94 | 0 | <0.12 | <0.12 | 11 | 0.27 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,Humphreys Bungalow, St Bernards Rd | 2017-05-22 | 2017/Q2/2 | 1446770 |  | <0.024 | 13 | 0.014 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.62 | <0.30 | <0.0090 | 210 | 0.29 | <0.93 | 740 | 0.0009 | <1.7 | <0.10 | <0.024 | <1.2 | 0.21 | <0.18 | <0.011 | 0.4 | <1.7 | <0.0029 | 0 | <0.17 | 0.012 | 8.15 | 0 | <0.42 | 97 | 6.85 | 0 | <0.12 | <0.12 | 0 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Middle Hill Res, Upper Rock, Devils Gap | 2017-05-22 | 2017/Q2/3 | 1446771 |  | <0.024 | 9.4 | 0.015 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.63 | <0.30 | <0.0090 | 200 | 0.23 | <0.93 | 730 | <0.00070 | <1.7 | <0.10 | <0.024 | <1.2 | 0.08 | <0.18 | <0.011 | 0.084 | <1.7 | <0.0029 | 0 | <0.17 | 0.0079 | 8.2 | 0 | <0.42 | 91 | 5.33 | 0 | <0.12 | <0.12 | 0 | 0.095 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,West Side District,Harbour Views Road | 2017-07-31 | 2017/Q3/1 | 1493861 |  | <0.024 | 12 | <0.0072 | <0.080 | 0.065 | <0.013 | <0.00056 | 0.57 | <0.30 | <0.0090 | 180 | 0.3 | <0.93 | 640 | 0.0009 | <1.7 | <0.10 | <0.024 | 7.9 | 0.52 | 0.23 | <0.011 | 0.28 | <1.7 | <0.0029 | 0 | 0.26 | 0.017 | 8.07 | 0 | <0.42 | 81 | 3.77 | 0 | <0.12 | <0.12 | 2.5 | 0.098 | <0.50 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District,Lynx FC | 2017-07-31 | 2017/Q3/2 | 1493867 |  | <0.024 | 11 | <0.0072 | <0.080 | 0.028 | <0.013 | <0.00056 | 0.51 | <0.30 | <0.0090 | 180 | 0.33 | <0.93 | 630 | <0.00070 | <1.7 | <0.10 | <0.024 | 1.7 | 0.29 | <0.18 | <0.011 | 0.32 | <1.7 | <0.0029 | 0 | 0.32 | 0.013 | 8.02 | 0 | <0.42 | 75 | 4.26 | 0 | <0.12 | <0.12 | 0 | 0.13 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Middle Hill Res, Upper Rock, Poca Roca Filter Room | 2017-10-23 | 2017/Q4/1 | 1549544 |  | <0.024 | 45 | <0.0072 | <0.080 | 0.026 | <0.013 | <0.00056 | 0.6 | <0.30 | <0.0090 | 170 | 1 | <0.93 | 600 | <0.00070 | <1.7 | <0.10 | <0.024 | <1.2 | 0.14 | <0.18 | <0.011 | <0.035 | <1.7 | <0.0029 | 0 | 0.19 | 0.037 | 8.09 | 0 | <0.42 | 72 | 2.65 | 0 | <0.12 | <0.12 | 0 | 0.15 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2,MC Res,Low Level,36 Macintosh Square | 2017-10-23 | 2017/Q4/2 | 1549545 |  | <0.024 | 14 | <0.0072 | <0.080 | 0.027 | <0.013 | <0.00056 | 0.56 | 11 | <0.0090 | 180 | 0.31 | <0.93 | 620 | 0.0024 | <1.7 | <0.10 | <0.024 | 38 | 0.51 | 0.41 | <0.011 | 0.29 | <1.7 | <0.0029 | 0 | 0.19 | 0 | 7.79 | 0 | <0.42 | 68 | 1.79 | 0 | <0.12 | <0.12 | 2.3 | 0.14 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply,supply meter box, bottom Mount Road | 2017-10-23 | 2017/Q4/3 | 1549546 |  | <0.024 | 15 | <0.0072 | <0.080 | 0.033 | <0.013 | <0.00056 | 0.59 | <0.30 | <0.0090 | 170 | 1.1 | <0.93 | 590 | <0.00070 | <1.7 | <0.10 | <0.024 | <1.2 | 0.2 | <0.18 | <0.011 | <0.035 | <1.7 | <0.0029 | 0 | <0.17 | 0.0318 | 8.1 | 0 | <0.42 | 71 | 2.84 | 0 | <0.12 | <0.12 | 0 | 0.098 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,North Front,Beach View Terraces Res,D.T.road | 2018-01-29 | 2018/Q1/1 | 1609237 |  | <0.024 | 16 | 0.015 | <0.080 | 0.039 | <0.013 | <0.00056 | 0.7 | <0.30 | <0.0090 | 200 | 1.2 | <0.93 | 690 | 0.0013 | <1.7 | <0.10 | <0.024 | 14 | 0.87 | 0.27 | <0.011 | 0.55 | <1.7 | <0.0029 | 0 | 0.19 | 0 | 8.17 | 0 | <0.42 | 96 | 3.45 | 0 | <0.12 | <0.12 | 1.9 | 0.11 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3, Europa District,Europa Express, Europa Point | 2018-01-29 | 2018/Q1/2 | 1609238 |  | <0.024 | 12 | 0.017 | <0.080 | 0.044 | <0.013 | <0.00056 | 0.69 | <0.30 | 0.052 | 210 | 1.2 | <0.93 | 690 | 0.016 | <1.7 | <0.10 | <0.024 | <1.2 | 2.7 | <0.18 | <0.011 | 0.99 | <1.7 | <0.0029 | 0 | 0.51 | 0 | 8.18 | 0 | <0.42 | 98 | 4.46 | 0 | <0.12 | <0.12 | 0 | 0.045 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Jews Gate public toilet | 2018-04-17 | 2018/Q2/1 | 1652868 |  | <0.024 | 18 | 0.016 | <0.080 | 0.048 | 0.017 | <0.00056 | 0.6 | <0.30 | <0.0090 | 190 | 1.2 | <0.93 | 720 | 0.0007 | <1.7 | <0.10 | <0.024 | 1.3 | 0.2 | <0.18 | <0.011 | <0.035 | <1.7 | <0.0029 | 0 | 0.32 | 0 | 8.22 | 0 | <0.42 | 91 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.042 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Middle Hill Res, Upper Rock, Lower Bruces Farm | 2018-04-17 | 2018/Q2/2 | 1652869 |  | <0.024 | 21 | 0.018 | <0.080 | 0.12 | 0.018 | <0.00056 | 0.6 | <0.30 | 0.16 | 190 | 0.97 | <0.93 | 680 | 0.029 | <1.7 | <0.10 | <0.024 | 340 | 11 | 5.5 | <0.011 | 5.6 | <1.7 | <0.0029 | 0 | 0.44 | 0 | 8.18 | 0 | <0.42 | 90 | <0.19 | 0 | <0.12 | <0.12 | 0 | 1.7 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2, MC Res, Low Level, 41 Town Range | 2018-04-17 | 2018/Q2/3 | 1652870 |  | <0.024 | 14 | 0.016 | <0.080 | 0.057 | <0.013 | 0.001 | 0.78 | 4.1 | 0.013 | 190 | 1.3 | <0.93 | 660 | 0.011 | <1.7 | <0.10 | <0.024 | 160 | 6.9 | 9.1 | <0.011 | 1.1 | <1.7 | <0.0029 | 0 | 0.38 | 0 | 7.98 | 0.00354 | <0.42 | 89 | 1.76 | 0 | <0.12 | <0.12 | 3.1 | 0.5 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,Shipping, Aquagib RO Plant Canteen. | 2018-08-01 | 2018/Q3/1 | 1718067 |  | <0.024 | 10 | 0.0077 | <0.080 | 0.065 | <0.013 | <0.00056 | 0.56 | <0.30 | <0.0090 | 180 | 1.1 | <0.93 | 660 | 0.0035 | <1.7 | <0.10 | <0.024 | 3.8 | 4.1 | <0.18 | <0.011 | 16 | <1.7 | <0.0029 | 0 | <0.17 | 0 | 8.17 | 0 | <0.42 | 88 | <0.19 | 0 | <0.12 | <0.12 | 0.95 | 0.056 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3,Europa District, High Cliffs House | 2018-08-01 | 2018/Q3/2 | 1718070 |  | <0.024 | 11 | <0.0072 | <0.080 | 0.025 | <0.013 | <0.00056 | 0.6 | <0.30 | <0.0090 | 170 | 1.1 | <0.93 | 630 | 0.0017 | <1.7 | <0.10 | <0.024 | <1.2 | 0.48 | <0.18 | <0.011 | 0.28 | <1.7 | <0.0029 | 0 | <0.17 | 0 | 8.26 | 0 | <0.42 | 100 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.084 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Middle Hill Res, Upper Rock, Poca Roca Filter Room | 2018-10-22 | 2018/Q4/1 | 1766375 |  | <0.024 | 12 | <0.0072 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.65 | <0.10 | 0.012 | 190 | 1.5 | <1.10 | 680 | 0.011 | <1.7 | <0.10 | <0.024 | 1.8 | 7 | 0.46 | <0.011 | 0.79 | <1.7 | <0.0029 | 0 | 0.22 | 0 | 8.12 | 0 | <0.42 | 85 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.069 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, British Lines Road, Airport carpark | 2018-10-22 | 2018/Q4/2 | 1766378 |  | <0.024 | 12 | 0.0084 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.67 | <0.10 | <0.0090 | 190 | 1.6 | <1.10 | 690 | 0.0033 | <1.7 | <0.10 | <0.024 | 2.5 | 2.7 | 0.24 | <0.011 | 1.1 | <1.7 | <0.0029 | 0 | 0.35 | 0 | 8.24 | 0 | <0.42 | 90 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.069 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2, MC Res, Low Level, John Mac Sq meter box | 2018-10-22 | 2018/Q4/3 | 1766383 |  | <0.024 | 23 | 0.019 | <0.080 | 0.11 | <0.013 | <0.00056 | 0.62 | 8.9 | 0.011 | 190 | 1.2 | <0.93 | 650 | 0.011 | <1.7 | <0.10 | <0.024 | 380 | 2.5 | 5 | <0.011 | 0.48 | <1.7 | <0.0029 | 0 | 0.25 | 0.11 | 8 | 0.00277 | <0.42 | 74 | <0.19 | 0 | <0.12 | <0.12 | 9.3 | 1.1 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,High Level,No26 Flat Bastion Road | 2019-01-30 | 2019/Q1/1 | 1824571 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.054 | 0.022 | <0.0019 | 0.67 | <0.30 | <0.0090 | 190 | 0.18 | <1.10 | 690 | 0.0015 | <1.7 | <0.10 | 0.028 | 5.5 | 0.32 | <0.18 | <0.011 | 0.2 | <1.7 | <0.0029 | 0 | 0.22 | 0 | 8.17 | 0 | <0.42 | 86 | <0.19 | 0 | <0.12 | <0.12 | 0.72 | 0.096 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3, Europa District,Block 23, Eliotts Battery | 2019-01-30 | 2019/Q1/2 | 1824574 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.049 | 0.022 | <0.0019 | 0.68 | <0.30 | 0.015 | 190 | 0.17 | 1.3 | 700 | 0.0022 | <1.7 | <0.10 | 0.028 | <1.2 | 0.78 | <0.18 | <0.011 | 0.87 | <1.7 | <0.0029 | 0 | 0.29 | 0 | 8.1 | 0 | <0.42 | 92 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.061 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2, MC Res, Low Level, Chatham Counterguard | 2019-04-15 | 2019/Q2/1 | 1870299 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.054 | 0.028 |  | 0.76 | 12 | 0.0091 | 190 | 0.29 | <1.10 | 670 | 0.0031 | <1.7 | <0.10 | 0.028 | 37 | 0.4 | 0.51 | <0.011 | 0.29 | <1.7 | <0.0029 | 0 | <0.17 | 0 | 7.99 | 0 | <0.42 | 80 | <0.19 | 0 | <0.12 | <0.12 | 2.9 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Middle Hill Res, Upper Rock, Devils Gap | 2019-04-15 | 2019/Q2/2 | 1870300 |  | <0.024 | 11 | <0.0072 | <0.080 | 0.025 | <0.013 | <0.00056 | 0.6 | <0.30 | <0.0090 | 170 | 1.1 | <0.93 | 630 | 0.0017 | <1.7 | <0.10 | <0.024 | <1.2 | 0.48 | <0.18 | <0.011 | 0.28 | <1.7 | <0.0029 | 0 | <0.17 | 0 | 8.26 | 0 | <0.42 | 100 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.084 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Retreat Centre | 2019-04-15 | 2019/Q2/3 | 1870301 |  | <0.024 | 23 | 0.019 | <0.080 | 0.11 | <0.013 | <0.00056 | 0.62 | 8.9 | 0.011 | 190 | 1.2 | <0.93 | 650 | 0.011 | <1.7 | <0.10 | <0.024 | 380 | 2.5 | 5 | <0.011 | 0.48 | <1.7 | <0.0029 | 0 | 0.25 | 0.11 | 8 | 0.00277 | <0.42 | 74 | <0.19 | 0 | <0.12 | <0.12 | 9.3 | 1.1 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3, Europa District,Brympton, the Mount | 2019-07-23 | 2019/Q3/1 | 1926623 |  | <0.024 | 12 | 0.0084 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.67 | <0.10 | <0.0090 | 190 | 1.6 | <1.1 | 690 | 0.0033 | <1.7 | <0.10 | <0.024 | 2.5 | 2.7 | 0.24 | <0.011 | 1.1 | <1.7 | <0.0029 | 0 | 0.35 | 0 | 8.24 | 0 | <0.42 | 90 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.069 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,South District Transport Road,Vinyards | 2019-07-23 | 2019/Q3/2 | 1926638 |  | <0.024 | 12 | <0.0072 | <0.080 | <0.023 | <0.013 | <0.00056 | 0.65 | <0.10 | 0.012 | 190 | 1.5 | <1.1 | 680 | 0.011 | <1.7 | <0.10 | <0.024 | 1.8 | 7 | 0.46 | <0.011 | 0.79 | <1.7 | <0.0029 | 0 | 0.22 | 0 | 8.12 | 0 | <0.42 | 85 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.069 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone2, MC Res, L L, Castle Rd, John mackintosh Home | 2019-10-21 | 2019/Q4/1 | 1984324 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.054 | 0.022 | <0.0019 | 0.67 | <0.30 | <0.0090 | 190 | 0.18 | <1.1 | 690 | 0.0015 | <1.7 | <0.10 | 0.028 | 5.5 | 0.32 | <0.18 | <0.011 | 0.2 | <1.7 | <0.0029 | 0 | 0.22 | 0 | 8.17 | 0 | <0.42 | 86 | <0.19 | 0 | <0.12 | <0.12 | 0.72 | 0.096 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone4,Middle Hill Res, Upper Rock, Devils Gap | 2019-10-21 | 2019/Q4/2 | 1984325 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.049 | 0.022 | <0.0019 | 0.68 | <0.30 | 0.015 | 190 | 0.17 | 1.3 | 700 | 0.0022 | <1.7 | <0.10 | 0.028 | <1.2 | 0.78 | <0.18 | <0.011 | 0.87 | <1.7 | <0.0029 | 0 | 0.29 | 0 | 8.1 | 0 | <0.42 | 92 | <0.19 | 0 | <0.12 | <0.12 | 0 | 0.061 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Governors Cottage, RO Palnt canteen | 2019-10-21 | 2019/Q4/3 | 1984326 |  | <0.024 | <6.6 | <0.0072 | <0.080 | 0.054 | 0.028 | <0.0019 | 0.76 | 12 | 0.0091 | 190 | 0.29 | <1.1 | 670 | 0.0031 | <1.7 | <0.10 | 0.028 | 37 | 0.4 | 0.51 | <0.011 | 0.29 | <1.7 | <0.0029 | 0 | <0.17 | 0 | 7.99 | 0 | <0.42 | 80 | <0.19 | 0 | <0.12 | <0.12 | 2.9 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
WPRO Plant Production at Waterworks | 2020-02-24 | 2020/Q1/1 | 2059642 |  | <0.079 | 21 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.51 | <0.99 | <0.018 | 190 | <0.17 | 4.3 | 630 | <0.0014 | <5.5 | <0.10 | <0.060 | <2.3 | 0.11 | <0.36 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | 0.32 | 0 | 8.36 | 0 | <0.83 | 55 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.05 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone3, Europa District,The Cliftons | 2020-02-24 | 2020/Q1/2 | 2059644 |  | <0.079 | <14 | <0.015 | <0.16 | <0.46 | <0.041 | <0.0019 | 0.65 | <0.99 | <0.18 | 190 | <0.17 | 4.5 | 670 | <0.0014 | <5.5 | <0.10 | <0.060 | <2.3 | 0.092 | <0.36 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8.15 | 0 | <0.83 | 91 | <0.38 | 0 | <0.39 | <0.40 | 0 | <0.046 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone1,Westside Infrastructure Queensway | 2020-02-24 | 2020/Q1/3 | 2059646 |  | <0.079 | <14 | <0.015 | <0.16 | <0.46 | <0.041 | <0.0019 | 0.62 | <0.99 | <0.18 | 190 | <0.17 | <2.1 | 670 | 0.0049 | <5.5 | <0.10 | <0.060 | 24 | 2.4 | 0.38 | <0.022 | 0.21 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8.17 | 0 | <0.83 | 79 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.08 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Middle Hill Reservoir, Upper Rock, Lower Bruces Farm | 2020-07-20 | 2020/Q2/1 | 2138076 |  | <0.079 | <14 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.91 | <0.99 | <0.018 | 210 | <0.17 | <2.1 | 730 | 0.0043 | <5.5 | <0.10 | <0.060 | <2.3 | 2.6 | <0.36 | <0.022 | 0.5 | <3.3 | <0.0058 | 0 | 0.51 | 0 | 8.2 | 0 | <0.83 | 110 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Low Level District, Rock on the Rock Club, 41 Town Range | 2020-07-20 | 2020/Q2/2 | 2138078 |  | <0.079 | <14 | <0.015 | <0.16 | 0.054 | <0.041 | <0.0019 | 0.76 | <0.99 | <0.018 | 200 | <0.17 | <2.1 | 670 | 0.0023 | <5.5 | <0.10 | <0.060 | 6.4 | 1.9 | <0.36 | <0.022 | 0.39 | <3.3 | <0.0058 | 0 | 0.13 | 0 | 8.08 | 0 | <0.83 | 92 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.12 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Land Frontier Entrance to Runway Tunnel | 2020-07-20 | 2020/Q2/3 | 2138082 |  | <0.079 | <14 | <0.015 | <0.16 | 0.059 | <0.041 | <0.0019 | 0.77 | 26 | <0.018 | 280 | <0.17 | <2.1 | 950 | <0.0014 | <5.5 | <0.10 | <0.060 | 31 | 0.14 | <0.36 | 0.028 | 0.28 | <3.3 | <0.0058 | 0 | 0.19 | 0 | 7.95 | 0 | <0.83 | 130 | <0.38 | 0 | <0.39 | <0.40 | 2.3 | 0.13 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, North Front District, La Patisserie, Halifax Road | 2020-10-20 | 2020/Q3/1 | 2196015 |  | <0.079 | <14 | <0.015 | <0.16 | 0.12 | <0.041 | <0.0019 | 0.63 | <0.99 | <0.018 | 200 | <0.17 | <2.1 | 700 | <0.0014 | <5.5 | <0.10 | <0.060 | 9.2 | 0.11 | 0.41 | <0.022 | 0.18 | <3.3 | <0.0058 | 0 | 0.42 | 0 | 8.12 | 0 | <0.83 | 80 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.062 | <1.1 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Europa District, 22 Eliotts Battery, Eliotts Close | 2020-10-20 | 2020/Q3/2 | 2196016 |  | <0.079 | <14 | <0.015 | <0.16 | 0.058 | <0.041 | <0.0019 | 0.62 | <0.99 | <0.018 | 190 | <0.17 | <2.1 | 720 | <0.0014 | <5.5 | <0.10 | <0.060 | <2.3 | 0.18 | <0.36 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | 0.54 | 0 | 8.3 | 0 | <0.83 | 100 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.074 | <1.2 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Governors Cottage Reverse Osmosis Plant at Waterworks | 2020-10-20 | 2020/Q3/3 | 2196018 |  | <0.079 | <14 | <0.015 | <0.16 | 0.061 | <0.041 | <0.0019 | 0.63 | <0.99 | <0.018 | 180 | <0.17 | <2.1 | 620 | <0.0014 | <5.5 | <0.10 | <0.060 | <2.3 | 0.33 | <0.36 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | 0.29 | 0 | 8.19 | 0 | <0.83 | 80 | <0.38 | 0 | <0.39 | <0.40 | 0 | 0.051 | <1.3 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Lower Level District, No 54 Irish Town | 2020-12-01 | 2020/Q4/1 | 2225548 |  | <0.079 | <14 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.64 | <0.99 | <0.018 | 200 | <0.17 | <2.3 | 700 | <0.0014 | <5.5 | <0.10 | <0.060 | 6.8 | 0.85 | 0.38 | <0.022 | 0.49 | <3.3 | <0.0058 | 0 | 0.57 | 0.0051 | 8.13 | 0 | <0.83 | 82 | <0.38 | 0 | <0.39 | <0.40 | 0 | <0.090 | <1.4 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Middle Hill Reservoir, Upper Rock, Poca Roca Filter Room | 2020-12-01 | 2020/Q4/2 | 2225549 |  | <0.079 | <14 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.66 | <0.99 | <0.018 | 200 | <0.17 | <2.3 | 710 | 0.0014 | <5.5 | <0.10 | <0.060 | <2.3 | 0.62 | <0.36 | <0.022 | 1.7 | <3.3 | <0.0058 | 0 | 0.38 | 0.0025 | 8.11 | 0 | <0.83 | 85 | <0.38 | 0 | <0.39 | <0.40 | 0 | <0.090 | <1.5 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Waterport Reverse Omosis Production Waterworks | 2021-04-12 | 2021/Q1/1 | 2298107 |  | <0.079 | <3.9 | 0.016 | <0.16 | 0.058 | <0.041 | <0.0019 | 0.56 | <0.99 | <0.018 | 190 | <0.17 | <2.3 | 620 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.093 | <0.28 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | 0.48 | 0 | 8.02 | 0 | <0.83 | 62 | <0.074 | 0 | <0.39 | <0.40 | 0 | 0.096 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, Shipping District, Water supply to Shipping | 2021-04-12 | 2021/Q1/2 | 2298111 |  | <0.079 | 6.5 | <0.015 | <0.16 | 0.098 | <0.041 | <0.0019 | 0.58 | <0.99 | <0.018 | 200 | <0.17 | <2.3 | 670 | <0.0014 | <5.5 | <0.10 | <0.060 | 83 | 0.19 | 1.7 | <0.022 | 0.13 | <3.3 | <0.0058 | 0 | 5.6 | 0 | 8.09 | 0 | <0.83 | 73 | 0.44 | 0 | <0.39 | <0.40 | 0 | 0.25 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Europa District, Buena Vista Villas | 2021-04-12 | 2021/Q1/3 | 2298124 |  | <0.079 | <3.9 | <0.015 | <0.16 | 0.058 | <0.041 | <0.0019 | 0.64 | <0.99 | <0.018 | 210 | <0.17 | <2.3 | 710 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.53 | <0.28 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | 0.73 | 0 | 8.12 | 0 | <0.83 | 88 | 1.1 | 0 | <0.39 | <0.40 | 0 | 0.092 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Low Level District, Governor's Parade | 2021-07-27 | 2021/Q2/1 | 2364705 |  | <0.079 | <3.9 | <0.015 | <0.16 | 0.063 | <0.041 | <0.0019 | 0.6 | <0.99 | 0.024 | 200 | <0.17 | <2.3 | 690 | 0.011 | <5.5 | <0.10 | <0.060 | 14 | 3.6 | 0.39 | <0.022 | 0.44 | <3.3 | <0.0058 | 0 | 0.35 | 0 | 8.1 | 0 | <0.83 | 91 | 4.5 | 0 | <0.39 | <0.40 | 0 | 0.4 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Upper Rock Devil's Gap | 2021-07-27 | 2021/Q2/2 | 2364706 |  | <0.079 | 4.2 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.62 | <0.99 | <0.018 | 190 | <0.17 | <2.3 | 650 | 0.011 | <5.5 | <0.10 | <0.060 | <5.2 | 2.1 | <0.28 | <0.022 | 0.82 | <3.3 | <0.0058 | 0 | 0.22 | 0 | 8.26 | 0 | <0.83 | 88 | 2.5 | 0 | <0.39 | <0.40 | 0 | 0.11 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD, North Front, Bureaux de Exchange | 2021-07-27 | 2021/Q2/3 | 2364707 |  | <0.079 | 7.7 | <0.015 | <0.16 | 0.078 | <0.041 | <0.0019 | 0.58 | 25 | 0.019 | 190 | <0.17 | <2.3 | 660 | 0.0078 | <5.5 | <0.10 | <0.060 | 180 | 2.7 | 9 | <0.022 | 0.84 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 7.96 | 0 | <0.83 | 73 | 1.1 | 0 | <0.39 | <0.40 | 0 | 0.38 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, High Level District, Flat Bastion Road | 2021-10-04 | 2021/Q3/1 | 2411848 |  | <0.079 | <3.9 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.79 | <0.99 | <0.018 | 210 | <0.17 | <0.81 | 700 | 0.0036 | <5.5 | <0.10 | <0.060 | 6.2 | 3.8 | <0.28 | <0.022 | 0.13 | <3.3 | <0.0058 | 0 | 0.44 | 0 | 8.1 | 0 | <0.83 | 90 | <0.074 | 0 | <0.39 | <0.40 | 2.5 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone , Europa Distict, Lync F.C. | 2021-10-04 | 2021/Q3/2 | 2411907 |  | <0.079 | 11 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.68 | 16 | <0.018 | 200 | <0.17 | <0.81 | 680 | 0.0017 | <5.5 | <0.10 | <0.060 | <5.2 | 1.7 | <0.28 | <0.022 | 0.3 | <3.3 | <0.0058 | 0 | 0.7 | 0 | 8 | 0 | <0.83 | 78 | <0.074 | 0 | <0.39 | <0.40 | 0 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Governors Cottage Reverse Osmosis Plant at Waterworks | 2021-10-04 | 2021/Q3/3 | 2411912 |  | <0.079 | <3.9 | <0.015 | <0.16 | <0.046 | <0.041 | <0.0019 | 0.75 | <0.99 | <0.018 | 210 | <0.17 | <0.81 | 700 | 0.0015 | <5.5 | <0.10 | <0.060 | <5.2 | 0.29 | <0.28 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8.1 | 0 | <0.83 | 91 | <0.074 | 0 | <0.39 | <0.40 | 0 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Middle Hill Reservoir, Upper, Lower Bruces Farm | 2021-11-01 | 2021/Q4/1 | 2432823 |  | <0.079 | <3.9 | <0.015 | <0.16 | 0.06 | <0.041 | <0.0019 | 0.72 | <0.99 | <0.018 | 190 | <0.17 | <0.81 | 670 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.23 | <0.28 | <0.022 | 0.15 | <3.3 | <0.0058 | 0 | 0.82 | 0 | 8.2 | 0 | <0.83 | 91 | 2.1 | 0 | <0.39 | <0.40 | 0 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Moorish Castle, Low Level District, City Mill Lane | 2021-11-01 | 2021/Q4/2 | 2432834 |  | <0.079 | <3.9 | <0.015 | <0.16 | 0.061 | <0.041 | <0.0019 | 0.69 | <0.99 | <0.018 | 190 | <0.17 | <0.81 | 660 | <0.0014 | <5.5 | <0.10 | <0.060 | 16 | 4.1 | 0.46 | <0.022 | 0.19 | <3.3 | <0.0058 | 0 | 0.56 | 0 | 8.2 | 0 | <0.83 | 88 | 3 | 0 | <0.39 | <0.40 | 0 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD, South Entrance, Upper Rock Nature Reserve | 2021-11-01 | 2021/Q4/3 | 2432840 |  | <0.079 | <3.9 | <0.015 | <0.16 | 0.066 | <0.041 | <0.0019 | 0.69 | 26 | <0.018 | 190 | 0.24 | <0.81 | 680 | 0.0029 | <5.5 | <0.10 | <0.060 | 29 | 0.27 | 0.45 | <0.022 | 0.28 | <3.3 | <0.0058 | 0 | 0.63 | 0 | 8.1 | 0 | <0.83 | 79 | 1.2 | 0 | <0.39 | <0.40 | 9.9 | 0.092 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, South District, New Harbours Industrial Park | 2022-01-24 | 2022/Q1/1 | 2482413 |  | <0.20 | <3.9 | 0.034 | <0.16 | <0.046 | 0.091 | <0.0019 | 0.67 | <0.90 | <0.018 | 200 | <0.17 | <0.81 | 700 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.24 | <0.28 | <0.022 | 0.21 | <3.3 | <0.0058 | 0 | 0.35 | 0 | 8.2 | 0 | <0.83 | 84 | 1.5 | 0 | <0.16 | <0.13 | 1.6 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Europa District, Europa Point | 2022-01-24 | 2022/Q1/2 | 2482416 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | 0.083 | <0.0019 | 0.67 | <0.90 | <0.018 | 210 | <0.17 | <0.81 | 710 | 0.0025 | <5.5 | <0.10 | <0.060 | 57 | 2.4 | 1.7 | <0.022 | 0.22 | <3.3 | <0.0058 | 0 | 0.47 | 0 | 8.2 | 0 | <0.83 | 86 | 1.4 | 0 | <0.16 | <0.13 | 0.77 | 0.67 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Governors Cottage Reverse Osmosis Plant at Waterworks | 2022-01-24 | 2022/Q1/3 | 2482418 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.67 | <0.90 | <0.018 | 200 | <0.17 | <0.81 | 670 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.42 | <0.28 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8.2 | 0 | <0.83 | 85 | 1.4 | 0 | <0.16 | <0.13 | 0 | <0.090 | <1.0 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Low Level, District 9, London Bar | 2002-04-11 | 2022/Q2/1 | 2525663 |  | <0.20 | 8.1 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.61 | <0.99 | <0.018 | 250 | <0.17 | <0.81 | 860 | <0.0014 | <5.5 | <0.10 | <0.060 | 27 | 1.1 | 0.69 | <0.022 | 0.66 | <3.3 | <0.0058 | 0 | 0.38 | 0 | 8 | 0 | <0.83 | 110 | 5.1 | 0 | <0.16 | <0.13 | 7.9 | 0.31 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Bleak House | 2002-04-11 | 2022/Q2/2 | 2525667 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.51 | 12 | <0.018 | 190 | <0.17 | <0.81 | 670 | <0.0014 | <5.5 | <0.10 | <0.060 | 14 | 0.21 | 0.45 | <0.022 | 0.34 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8 | 0 | <0.83 | 73 | <0.074 | 0 | <0.16 | <0.13 | 6.1 | 0.098 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Waterport Reverse Omosis Production Waterworks | 2002-04-11 | 2022/Q2/3 | 2525670 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.52 | <0.99 | <0.018 | 190 | <0.17 | <0.81 | 610 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.18 | 1.2 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 7.9 | 0 | <0.83 | 50 | <0.074 | 0 | <0.16 | <0.13 | 0 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Reverse Osmosis, Waterport Plant At Waterworks | 2022-07-18 | 2022/Q3/1 | 2583188 |  | <0.20 | <3.9 | <0.015 | <0.16 | 0.062 | <0.030 | <0.0019 | 0.87 | <0.50 | <0.018 | 180 | <0.17 | <0.81 | 580 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.13 | <0.28 | <0.022 | <0.069 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8.2 | 0 | <0.83 | 72 | <0.074 | 0 | <0.16 | <0.13 | 0.74 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, Shipping, District 19, Water Desalination Platn | 2022-07-18 | 2022/Q3/2 | 2583189 |  | <0.20 | <3.9 | <0.015 | <0.16 | 0.062 | <0.030 | <0.0019 | 0.88 | <0.50 | <0.018 | 190 | <0.17 | <0.81 | 630 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.26 | 0.31 | <0.022 | 0.22 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 8.1 | 0 | <0.83 | 82 | <0.074 | 0 | <0.16 | <0.13 | 0.93 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, District 40, Buena Vista Park Villas | 2022-07-18 | 2022/Q3/3 | 2583190 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.89 | <0.50 | <0.018 | 200 | <0.17 | <0.81 | 650 | <0.0014 | <5.5 | <0.10 | <0.060 | 9.7 | 0.72 | <0.28 | 0.023 | 0.11 | <3.3 | <0.0058 | 0 | 0.27 | 0 | 8.1 | 0 | <0.83 | 88 | <0.074 | 0 | <0.16 | <0.13 | 0.79 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Low Level District 7, Piazza PW Drinking Fountains | 2022-10-25 | 2022/Q4/2 | 2643741 |  | <0.20 | <3.9 | <0.015 | <0.16 | 0.064 | <0.030 | <0.0019 | 0.98 | <0.50 | <0.018 | 190 | <0.17 | <0.81 | 650 | 0.0016 | <5.5 | <0.10 | <0.060 | 35 | 0.45 | 1.2 | <0.022 | 0.34 | <3.3 | <0.0058 | 0 | 0.26 | 0 | 8.2 | 0 | <0.83 | 95 | 1.2 | 0 | <0.16 | <0.13 | 1.6 | 0.13 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Airport Car Parks | 2022-10-25 | 2022/Q4/2 | 2643744 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.78 | 5.6 | 0.022 | 200 | <0.17 | <0.81 | 700 | 0.0014 | <5.5 | <0.10 | <0.060 | 150 | 0.88 | 1.9 | <0.022 | 0.11 | <3.3 | 0.016 | 0 | 0.32 | 0 | 8 | 0 | <0.83 | 100 | 6.8 | 0 | <0.16 | <0.13 | 1.9 | 0.16 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Middle Hill Reservoir, Upper Rock, Upper Galleries | 2022-10-25 | 2022/Q4/3 | 2643738 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.9 | <0.50 | <0.018 | 190 | <0.17 | <0.81 | 640 | 0.0022 | <5.5 | <0.10 | <0.060 | 13 | 1.7 | 1.3 | <0.022 | 0.16 | <3.3 | <0.0058 | 0 | 0.19 | 0 | 8 | 0 | <0.83 | 86 | 1.2 | 0 | <0.16 | <0.13 | 1 | 0.13 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Reverse Osmosis, Governors Cottage Plant | 2023-01-16 | 2023/Q1/1 | 2689286 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.82 | <0.50 | <0.018 | 200 | <0.17 | <0.81 | 660 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.23 | <0.28 | <0.022 | 0.58 | <3.3 | <0.0058 | 0 | 0.26 | 0 | 7.9 | 0 | <0.83 | 77 | 1.3 | 0 | <0.16 | <0.13 | 0 | 0.095 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, North Front, Cemetery Road | 2023-01-16 | 2023/Q1/2 | 2689288 |  | <0.20 | 6 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.64 | 16 | <0.018 | 200 | <0.17 | <0.81 | 610 | 0.0037 | <5.5 | <0.10 | <0.060 | 45 | 0.28 | 0.51 | <0.022 | 0.18 | <3.3 | <0.0058 | 0 | 0.19 | 0 | 8 | 0 | <0.83 | 81 | 3.8 | 0 | <0.16 | <0.13 | 4.1 | 0.31 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Jews Gate | 2023-01-16 | 2023/Q1/3 | 2689291 |  | <0.20 | <3.9 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.85 | 0.78 | <0.018 | 190 | <0.17 | <0.81 | 640 | <0.0014 | <5.5 | <0.10 | <0.060 | 14 | 0.81 | 0.32 | <0.022 | 0.33 | <3.3 | <0.0058 | 0 | 0.26 | 0 | 8.1 | 0 | <0.83 | 83 | 1.6 | 0 | <0.16 | <0.13 | 0 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Reverse Osmosis Waterport Plant @ Waterworks | 2023-04-17 | 2023/Q2/1 | 2738659 |  | <0.20 | 4.3 | <0.015 | <0.16 | 0.061 | <0.030 | <0.0019 | 0.88 | <0.50 | <0.018 | 190 | 0.53 | <0.81 | 630 | 0.022 | <5.5 | <0.10 | <0.060 | <5.2 | 0.78 | <0.28 | <0.022 | 0.52 | <3.3 | <0.0058 | 0 | 0.26 | 0 | 8 | 0 | <0.83 | 69 | 0.46 | 0 | <0.16 | <0.13 | 0 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, 84 Irish Town Meter Box | 2023-04-17 | 2023/Q2/2 | 2738662 |  | <0.20 | 5.2 | <0.015 | <0.16 | 0.057 | <0.030 | <0.0019 | 0.84 | 0.61 | <0.018 | 180 | 0.47 | <0.81 | 610 | <0.0014 | <5.5 | <0.10 | <0.060 | 15 | 0.79 | 0.33 | <0.022 | 0.35 | <3.3 | <0.0058 | 0 | <0.17 | 0 | 7.9 | 0 | <0.83 | 76 | 1.3 | 0 | <0.16 | <0.13 | 1.2 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Europa Point Meter Box | 2023-04-17 | 2023/Q2/3 | 2738663 |  | <0.20 | 4.5 | <0.015 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.82 | <0.50 | <0.018 | 180 | 0.74 | <0.81 | 600 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.51 | <0.28 | <0.022 | 0.47 | <3.3 | <0.0058 | 0 | 0.19 | 0 | 8.1 | 0 | <0.83 | 76 | 1.2 | 0 | <0.16 | <0.13 | 0 | <0.090 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Reverse Osmosis Governoers Cottage @ Waterworks | 2023-07-10 | 2023/Q3/1 | 2789434 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.81 | <0.50 | <0.018 | 190 | 0.37 | <0.81 | 620 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.18 | <0.28 | <0.022 | 0.25 | <1.5 | <0.0032 | 0 | <0.17 | 0 | 7.9 | 0 | <0.83 | 77 | 2.4 | 0 | <0.16 | <0.13 | 0 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, Moorish Castle Estate, Calpe House | 2023-07-10 | 2023/Q3/2 | 2789435 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.83 | <0.50 | <0.018 | 190 | 0.34 | <0.81 | 640 | <0.0014 | <5.5 | <0.10 | <0.060 | 33 | 1 | 1.7 | <0.022 | 0.31 | <1.5 | <0.0032 | 0 | 0.45 | 0 | 8 | 0 | <0.83 | 80 | 2.1 | 0 | <0.16 | <0.13 | 0 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, The Mount | 2023-07-10 | 2023/Q3/3 | 2789436 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0019 | 0.81 | <0.50 | <0.018 | 190 | 0.41 | <0.81 | 640 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.5 | 0.4 | <0.022 | 0.16 | <1.5 | <0.0032 | 0 | 0.51 | 0 | 7.9 | 0 | <0.83 | 79 | 2.4 | 0 | <0.16 | <0.13 | 0 | 0.42 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Engineers Lane | 2023-10-16 | 2023/Q4/1 | 2846689 |  | <0.20 | 6.3 | <0.020 | <0.16 | 0.1 | <0.030 | <0.0021 | 0.83 | <0.50 | 0.018 | 200 | <0.67 | <0.81 | 670 | 0.0089 | <5.5 | <0.10 | <0.060 | 400 | 3.9 | 4.2 | <0.022 | 0.66 | <1.5 | <0.0032 | 0 | 0.45 | 0 | 7.9 | 0 | <0.83 | 85 | <0.074 | 0 | <0.16 | <0.13 | 1.4 | 1.3 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Devil's Gap | 2023-10-16 | 2023/Q4/2 | 2846690 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0021 | 0.81 | <0.50 | <0.018 | 170 | <0.67 | <0.81 | 600 | 0.0054 | <5.5 | <0.10 | <0.060 | <5.2 | 22 | <0.28 | <0.022 | 2.3 | <1.5 | <0.0032 | 0 | 0.45 | 0 | 7.9 | 0 | <0.83 | 74 | <0.074 | 0 | <0.16 | <0.13 | 1.9 | 0.55 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply Jews Gate | 2023-10-16 | 2023/Q4/3 | 2846691 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0021 | 0.74 | 13 | <0.018 | 180 | <0.67 | <0.81 | 630 | 0.0018 | <5.5 | <0.10 | <0.060 | 40 | 0.23 | 0.64 | <0.022 | 0.25 | <1.5 | <0.0032 | 0 | 0.38 | 0 | 8 | 0 | <0.83 | 78 | <0.074 | 0 | <0.16 | <0.13 | 4.9 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
WPRO @ WW | 2023-10-16 | 2023/Q4/4 | 2846692 |  | <0.20 | <3.9 | <0.020 | <0.16 | 0.053 | <0.030 | <0.0021 | 0.73 | <0.50 | <0.018 | 200 | <0.67 | <0.81 | 690 | 0.0021 | <5.5 | <0.10 | <0.060 | <5.2 | 0.6 | <0.28 | <0.022 | 0.75 | <1.5 | <0.0032 | 0 | 0.45 | 0 | 8 | 0 | <0.83 | 82 | <0.074 | 0 | <0.16 | <0.13 | 1.2 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, Westside, Europort Road, GASA Meter Box | 2024-01-24 | 2024/Q1/1 | 2903809 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0021 | 0.7 | 1.3 | <0.018 | 170 | <0.67 | <0.81 | 580 | <0.0014 | <5.5 | <0.10 | <0.060 | 14 | 0.39 | <0.28 | <0.022 | 0.072 | <1.5 | <0.0032 | 0 | 0.26 | 0 | 7.9 | 0 | <0.83 | 68 | <0.074 | 0 | <0.16 | <0.13 | 1.5 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Bleak House Meter Box | 2024-01-24 | 2024/Q1/2 | 2903810 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0021 | 0.63 | 0.85 | <0.018 | 160 | <0.67 | <0.81 | 550 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 1.3 | <0.28 | <0.022 | <0.069 | <1.5 | <0.0032 | 0 | 0.32 | 0 | 7.9 | 0 | <0.83 | 60 | <0.074 | 0 | <0.16 | <0.13 | 0.65 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Governors Cottage Reverse Osmosis Plant at Waterworks | 2024-01-24 | 2024/Q1/3 | 2903811 |  | <0.20 | <3.9 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0021 | 0.61 | 0.77 | <0.018 | 150 | <0.67 | <0.81 | 510 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 0.38 | <0.28 | <0.022 | <0.069 | <1.5 | <0.0032 | 0 | 0.38 | 0 | 7.9 | 0 | <0.83 | 57 | <0.074 | 0 | <0.16 | <0.13 | 0 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Middle Hill Reservoir, Upper Rock, Devil's Gap | 2024-05-13 | 2024/Q2/1 | 2968468 |  | <0.20 | <12 | <0.020 | <0.16 | 0.051 | <0.030 | <0.0021 | 0.72 | <0.50 | <0.018 | 170 | <0.67 | <0.81 | 600 | 0.0026 | <5.5 | <0.10 | <0.060 | <5.2 | 0.55 | <0.28 | <0.022 | 0.11 | <1.5 | <0.0032 | 0 | 0.33 | 0 | 8 | 0 | <0.83 | 78 | <0.074 | 0 | <0.16 | <0.13 | 1.3 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Moorish Castle Low Level District, Governors Parade | 2024-05-13 | 2024/Q2/2 | 2968470 |  | <0.20 | <12 | <0.020 | <0.16 | 0.058 | <0.030 | <0.0021 | 0.71 | 1.7 | <0.018 | 200 | <0.67 | <0.81 | 670 | 0.0019 | <5.5 | <0.10 | <0.060 | 180 | 0.95 | 2.6 | <0.022 | 0.37 | <1.5 | <0.0032 | 0 | 0.33 | 0 | 8 | 0 | <0.83 | 87 | 2.1 | 0 | <0.16 | <0.13 | 2.1 | 0.35 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Waterport Reverse Omosis Production Waterworks | 2024-05-13 | 2024/Q2/3 | 2968471 |  | <0.20 | <12 | <0.020 | <0.16 | <0.046 | <0.030 | <0.0021 | 0.7 | <0.50 | <0.018 | 200 | <0.67 | <0.81 | 660 | 0.0054 | <5.5 | <0.10 | <0.060 | <5.2 | 1.3 | 0.31 | <0.022 | 0.4 | <1.5 | <0.0032 | 0 | 0.33 | 0 | 8.1 | 0 | <0.83 | 80 | 1.6 | 0 | <0.16 | <0.13 | 0 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, High Level, District 13, Elderly Residential Services (ERS), Castle Road | 2024-07-15 | 2024/Q3/1 | 3008502 |  | <0.20 | <12 | <0.020 | <0.16 | 0.05 | <0.030 | <0.0021 | 0.73 | 1.8 | <0.020 | 170 | <0.67 | <0.81 | 590 | <0.0014 | <5.5 | <0.10 | <0.060 | 23 | 0.42 | <0.28 | <0.022 | <0.069 | <1.5 | <0.0032 | 0 | 0.23 | 0 | 8 | 0 | <0.83 | 67 | <0.074 | 0 | <0.16 | <0.13 | 1.1 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Lathbury Reservoir | 2024-07-15 | 2024/Q3/2 | 3008509 |  | <0.20 | <12 | <0.020 | <0.16 | 0.05 | <0.030 | <0.0021 | 0.73 | <0.50 | <0.020 | 170 | <0.67 | <0.81 | 590 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 1.6 | <0.28 | <0.022 | 0.27 | <1.5 | <0.0032 | 0 | <0.17 | 0 | 8 | 0 | <0.83 | 72 | <0.074 | 0 | <0.16 | <0.13 | 0 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD supply, Lathbury Industrial Park | 2024-07-15 | 2024/Q3/3 | 3008512 |  | <0.20 | <12 | <0.020 | <0.16 | 0.05 | <0.030 | <0.0021 | 0.63 | 19 | <0.020 | 150 | <0.67 | <0.81 | 550 | 0.0023 | <5.5 | <0.10 | <0.060 | 32 | 2.1 | 0.47 | <0.022 | 0.14 | <1.5 | <0.0032 | 0 | <0.17 | 0 | 8.1 | 0 | <0.83 | 68 | <0.074 | 0 | <0.16 | <0.13 | 3.8 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, District 6, ICC | 2024-10-21 | 2024/Q4/1 | 3072862 |  | <0.20 | <12 | 0.31 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.76 | 1.4 | <0.018 | 190 | <0.67 | <0.81 | 630 | <0.0014 | <5.5 | <0.10 | <0.060 | 17 | 0.3 | <0.28 | <0.022 | 0.3 | <1.5 | <0.0061 | 0 | 0.48 | 0 | 7.9 | 0 | <0.83 | 76 | 0.34 | 0 | <0.16 | <0.13 | 3 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Poca Rocca | 2024-10-21 | 2024/Q4/2 | 3072868 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.74 | <0.50 | <0.018 | 170 | <0.67 | <0.81 | 610 | 0.0023 | <5.5 | <0.10 | <0.060 | <5.2 | 2.1 | <0.28 | <0.022 | 0.21 | <1.5 | <0.0061 | 0 | 0.61 | 0 | 8 | 0 | <0.83 | 69 | <0.074 | 0 | <0.16 | <0.13 | 1 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply Mount Alvenia | 2024-10-21 | 2024/Q4/3 | 3072870 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.67 | 15 | <0.018 | 170 | <0.67 | <0.81 | 610 | 0.0026 | <5.5 | <0.10 | <0.060 | 54 | 0.7 | 0.93 | <0.022 | 0.24 | <1.5 | <0.0061 | 0 | 0.35 | 0 | 8 | 0 | <0.83 | 73 | <0.074 | 0 | <0.16 | <0.13 | 4.6 | 0.29 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 1, South District, Cumberland Terraces | 2025-01-21 | 2025/Q1/1 | 3129430 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.65 | <0.50 | 0.025 | 170 | <0.67 | <0.81 | 570 | 0.0039 | <5.5 | <0.10 | <0.060 | 11 | 0.61 | <0.28 | <0.022 | 1.7 | <1.5 | <0.0061 | 0 | 0.44 | 0 | 8 | 0 | <0.83 | 65 | <0.074 | 0 | <0.16 | <0.13 | 2.5 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 3, Lathbury Reservoir | 2025-01-21 | 2025/Q1/2 | 3129431 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.65 | <0.50 | <0.018 | 180 | <0.67 | <0.81 | 570 | <0.0014 | <5.5 | <0.10 | <0.060 | <5.2 | 10) | <0.28 | <0.022 | 0.24 | <1.5 | <0.0061 | 0 | 2 | 0 | 7.9 | 0 | <0.83 | 66 | <0.074 | 0 | <0.16 | <0.13 | 0 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
WPRO @ WW | 2025-01-21 | 2025/Q1/3 | 3129432 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.6 | <0.50 | <0.018 | 160 | <0.67 | <0.81 | 520 | 0.0038 | <5.5 | <0.10 | <0.060 | <5.2 | 10) | <0.28 | <0.022 | 0.15 | <1.5 | <0.0061 | 0 | 2 | 0 | 8.1 | 0 | <0.83 | 53 | <0.074 | 0 | <0.16 | <0.13 | 0.75 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 2, Low Level District, Piazza Fountain | 2025-04-22 | 2025/Q2/1 | 3185884 |  | <0.20 | <12 | <0.020 | <0.16 | 0.06 | <0.030 | <0.0021 | 0.58 | 1.3 | <0.018 | 190 | 0.86 | <0.81 | 650 | 0.0031 | <5.5 | <0.10 | <0.038 | 120 | 10) | 3.6 | <0.022 | 0.51 | <1.5 | <0.0061 | 0 | 2 | 0 | 8 | 0 | <0.83 | 81 | 5 | 0 | <0.16 | <0.13 | 3.9 | 0.38 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
Zone 4, Upper Rock, Bruces Farm | 2025-04-22 | 2025/Q2/2 | 3185888 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.58 | <0.50 | <0.018 | 220 | <0.67 | <0.81 | 750 | <0.0014 | <5.5 | <0.10 | <0.038 | <5.2 | 10) | <0.28 | <0.022 | 0.21 | <1.5 | <0.0061 | 0 | 2 | 0 | 7.9 | 0 | <0.83 | 95 | 8.4 | 0 | <0.16 | <0.13 | 1.1 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
MOD Supply, Upper Rock, Jews Gate | 2025-04-22 | 2025/Q2/3 | 3185894 |  | <0.20 | <12 | <0.020 | <0.16 | <0.050 | <0.030 | <0.0021 | 0.59 | 10 | <0.018 | 150 | <0.67 | <0.81 | 570 | 0.002 | <5.5 | <0.10 | <0.038 | 28 | 10) | 0.36 | <0.022 | 0.16 | <1.5 | <0.0061 | 0 | 2 | 0 | 8.1 | 0 | <0.83 | 67 | 1 | 0 | <0.16 | <0.13 | 3.6 | <0.20 | <0.043 | <1 Not Detected | <1 Not Detected | <1 Not Detected
2025/Q3/1
2025/Q3/2
2025/Q3/3
2025/Q4/1
2025/Q4/2
2025/Q4/3

## Audit Results Extractor (hidden)
D odour (quantitative) 0.0 DN 5 HY | D odour (quantitative) | 0.0 | 1,2-Dichloroethane | D 1,2-Dichloroethane | <0.20
D benzo(a)pyrene <0.0021 ug/l HY-123 HN | D benzo(a)pyrene | <0.0021 | Aluminium | D aluminium | <12
D benzo(b)fluoranthene <0.0046 ug/l HY-123 HN | D benzo(b)fluoranthene | <0.0046 | ammonium | D ammonium | <0.020
D benzo(ghi)perylene <0.0022 ug/l HY-123 HN | D benzo(ghi)perylene | <0.0022 | Antimony | D Antimony | <0.16
D benzo(k)fluoranthene <0.0040 ug/l HY-123 HN | D benzo(k)fluoranthene | <0.0040 | Arsenic | D Arsenic | <0.050
D indeno(123cd)pyrene <0.0021 ug/l HY-123 HN | D indeno(123cd)pyrene | <0.0021 | Benzene | D Benzene | <0.030
D total PAH 0.00 ug/l HY-123 HN | D total PAH | 0.00 | Benzo(a)pyrene | D benzo(a)pyrene | <0.0021
* oxidizability as O2 0.38 mg/l O2 HY-216 HN | * oxidizability as O | 2 | Boron | D Boron | 0.59
D solids (total dissolved at 180C) 340 mg/l HY-225 HN | D solids (total dissolved at | 180C) | Bromate | D bromate | 10
D cyanide (total) <5.5 ug/l CN HY-243 HN | D cyanide (total) | <5.5 | Cadmium | D Cadmium | <0.018
D atrazine <0.0057 ug/l HY-264 HN | D atrazine | <0.0057 | Chloride | D chloride | 150
D chlorfenvinphos <0.0066 ug/l HY-264 HN | D chlorfenvinphos | <0.0066 | Chromium | D Chromium | <0.67
D chlorpyrifos <0.0070 ug/l HY-264 HN | D chlorpyrifos | <0.0070 | Colour | D Colour | <0.81
D diazinon <0.0074 ug/l HY-264 HN | D diazinon | <0.0074 | Conductivity | # electrical conductivity | 570
* dichlorvos <0.012 ug/l HY-264 HN | * dichlorvos | <0.012 | Copper | D Copper | 0.0020
D diflufenican <0.0072 ug/l HY-264 HN | D diflufenican | <0.0072 | Cyanide | D cyanide (total) | <5.5
D dimethoate <0.022 ug/l HY-264 HN | D dimethoate | <0.022 | Epichlorohydrin | * epichlorohydrin (subcontracted) | <0.10
D fenpropidin <0.011 ug/l HY-264 HN | D fenpropidin | <0.011 | Fluoride | # fluoride | <0.038
D fenpropimorph <0.0083 ug/l HY-264 HN | D fenpropimorph | <0.0083 | Iron | D Iron | 28
D malathion <0.0066 ug/l HY-264 HN | D malathion | <0.0066 | Lead | D lead (total - | 10)
D metalaxyl <0.0097 ug/l HY-264 HN | D metalaxyl | <0.0097 | Manganese | D Manganese | 0.36
D metazachlor <0.015 ug/l HY-264 HN | D metazachlor | <0.015 | Mercury | D Mercury | <0.022
D metribuzin <0.0060 ug/l HY-264 HN | D metribuzin | <0.0060 | Nickel | D Nickel | 0.16
D pendimethalin <0.0064 ug/l HY-264 HN | D pendimethalin | <0.0064 | Nitrate | D nitrate | <1.5
D phorate <0.0092 ug/l HY-264 HN | D phorate | <0.0092 | Nitrite | D nitrite | <0.0061
D pirimicarb <0.0063 ug/l HY-264 HN | D pirimicarb | <0.0063 | Odour | D odour (quantitative) | 0.0
D prometryn <0.0053 ug/l HY-264 HN | D prometryn | <0.0053 | Oxidisability | * oxidizability as O | 2
D propachlor <0.0096 ug/l HY-264 HN | D propachlor | <0.0096 | Pesticides- Total | * pesticides total (calculated) | 0.00
D propazine <0.0067 ug/l HY-264 HN | D propazine | <0.0067 | pH | # hydrogen ion (pH) | 8.1
D propetamphos <0.012 ug/l HY-264 HN | D propetamphos | <0.012 | Polycyclic Aromatic Hydrocarbons (PAH)Total | D total PAH | 0.00
D simazine <0.0067 ug/l HY-264 HN | D simazine | <0.0067 | Selenium | D Selenium | <0.83
D terbuthylazine <0.0069 ug/l HY-264 HN | D terbuthylazine | <0.0069 | Sodium | D Sodium | 67
D terbutryn <0.0047 ug/l HY-264 HN | D terbutryn | <0.0047 | Sulphate | D Sulphate | 1.0
D trietazine <0.0096 ug/l HY-264 HN | D trietazine | <0.0096 | Taste | Taste
D colour <0.81 mg/l Pt/Co scale HY266 HN | D colour | <0.81 | Tetrachloroethene | D Tetrachloroethene | <0.16
D antimony <0.16 ug/l Sb HY-267 HN | D antimony | <0.16 | Trichloroethene | D Trichloroethene | <0.13
D arsenic <0.050 ug/l As HY-267 HN | D arsenic | <0.050 | Trihalomethanes Total | D total THM | 3.6
D cadmium <0.018 ug/l Cd HY-267 HN | D cadmium | <0.018 | Turbidity | D Turbidity | <0.20
D chromium <0.67 ug/l Cr HY-267 HN | D chromium | <0.67 | Vinyl Chloride | D Vinyl Chloride | <0.043
D copper 0.0020 mg/l Cu HY-267 HN | D copper | 0.0020
D lead (total - 10) 0.27 ug/l Pb HY-267 HN | D lead (total - | 10)
D mercury <0.022 ug/l Hg HY-267 HN | D mercury | <0.022
D nickel 0.16 ug/l Ni HY-267 HN | D nickel | 0.16
D selenium <0.83 ug/l Se HY-267 HN | D selenium | <0.83
D silver <0.28 ug/l Ag HY-267 HN | D silver | <0.28
D zinc 8.1 ug/l Zn HY-267 HN | D zinc | 8.1
D carbetamide <0.0083 ug/l HY-270 HN | D carbetamide | <0.0083
D carbofuran <0.0023 ug/l HY-270 HN | D carbofuran | <0.0023
D chlortoluron <0.0031 ug/l HY-270 HN | D chlortoluron | <0.0031
D diuron <0.0055 ug/l HY-270 HN | D diuron | <0.0055
D ethofumesate <0.0070 ug/l HY-270 HN | D ethofumesate | <0.0070
D isoproturon <0.0025 ug/l HY-270 HN | D isoproturon | <0.0025
D linuron <0.0034 ug/l HY-270 HN | D linuron | <0.0034
D metamitron <0.0074 ug/l HY-270 HN | D metamitron | <0.0074
D methabenzthiazuron <0.0027 ug/l HY-270 HN | D methabenzthiazuron | <0.0027
D metoxuron <0.0080 ug/l HY-270 HN | D metoxuron | <0.0080
D monuron <0.0041 ug/l HY-270 HN | D monuron | <0.0041
D tebuthiuron <0.0020 ug/l HY-270 HN | D tebuthiuron | <0.0020
* 2,3,6-trichlorobenzoic acid <0.032 ug/l HY271 HN | * 2,3,6-trichlorobenzoic acid | <0.032
D 2,4,5-T <0.0085 ug/l HY271 HN | D 2,4,5-T | <0.0085
D 2,4-D <0.011 ug/l HY271 HN | D 2,4-D | <0.011
D 2,4-DB <0.016 ug/l HY271 HN | D 2,4-DB | <0.016
D benazolin <0.020 ug/l HY271 HN | D benazolin | <0.020
D bentazone <0.0044 ug/l HY271 HN | D bentazone | <0.0044
D bromoxynil <0.0079 ug/l HY271 HN | D bromoxynil | <0.0079
D chloridazon <0.013 ug/l HY271 HN | D chloridazon | <0.013
D clopyralid <0.0097 ug/l HY271 HN | D clopyralid | <0.0097
D dicamba <0.028 ug/l HY271 HN | D dicamba | <0.028
D dichlorprop <0.011 ug/l HY271 HN | D dichlorprop | <0.011
D fenoprop <0.011 ug/l HY271 HN | D fenoprop | <0.011
D fluroxypyr <0.0063 ug/l HY271 HN | D fluroxypyr | <0.0063
D ioxynil <0.0055 ug/l HY271 HN | D ioxynil | <0.0055
D lenacil <0.011 ug/l HY271 HN | D lenacil | <0.011
D MCPA <0.0093 ug/l HY271 HN | D MCPA | <0.0093
D MCPB <0.015 ug/l HY271 HN | D MCPB | <0.015
D MCPP <0.011 ug/l HY271 HN | D MCPP | <0.011
D pentachlorophenol <0.018 ug/l HY271 HN | D pentachlorophenol | <0.018
D picloram <0.026 ug/l HY271 HN | D picloram | <0.026
D propyzamide <0.012 ug/l HY271 HN | D propyzamide | <0.012
D triclopyr <0.012 ug/l HY271 HN | D triclopyr | <0.012
D turbidity <0.20 NTU HY-272 HN | D turbidity | <0.20
* surfactants <8.5 ug/l HY-274 HN | * surfactants | <8.5
D alachlor <0.0075 ug/l HY275 HN | D alachlor | <0.0075
D aldrin <0.0025 ug/l HY275 HN | D aldrin | <0.0025
D alpha-endosulphan <0.0059 ug/l HY275 HN | D alpha-endosulphan | <0.0059
D alpha-HCH <0.0062 ug/l HY275 HN | D alpha-HCH | <0.0062
D beta-endosulphan <0.0070 ug/l HY275 HN | D beta-endosulphan | <0.0070
D beta-HCH <0.0071 ug/l HY275 HN | D beta-HCH | <0.0071
D chlorthal-dimethyl <0.0052 ug/l HY275 HN | D chlorthal-dimethyl | <0.0052
D chlorthalonil <0.0071 ug/l HY275 HN | D chlorthalonil | <0.0071
D dichlobenil <0.0076 ug/l HY275 HN | D dichlobenil | <0.0076
D dieldrin <0.0019 ug/l HY275 HN | D dieldrin | <0.0019
D endrin <0.0088 ug/l HY275 HN | D endrin | <0.0088
D gamma-HCH (lindane) <0.012 ug/l HY275 HN | D gamma-HCH (lindane) | <0.012
D heptachlor <0.0018 ug/l HY275 HN | D heptachlor | <0.0018
D heptachlor-endo-epoxide <0.0043 ug/l HY275 HN | D heptachlor-endo-epoxide | <0.0043
D heptachlor epoxides 0.0 ug/l HY275 HN | D heptachlor epoxides | 0.0
D heptachlor-exo-epoxide <0.0039 ug/l HY275 HN | D heptachlor-exo-epoxide | <0.0039
D hexachlorobenzene <0.0065 ug/l HY275 HN | D hexachlorobenzene | <0.0065
D isodrin <0.0082 ug/l HY275 HN | D isodrin | <0.0082
D pentachlorobenzene <0.0048 ug/l HY275 HN | D pentachlorobenzene | <0.0048
D p,p-DDT <0.011 ug/l HY275 HN | D p,p-DDT | <0.011
D tecnazene <0.0065 ug/l HY275 HN | D tecnazene | <0.0065
D trifluralin <0.0052 ug/l HY275 HN | D trifluralin | <0.0052
D aluminium <12 ug/l Al HY276 HN | D aluminium | <12
D barium <0.47 ug/l Ba HY276 HN | D barium | <0.47
D boron 0.59 mg/l B HY276 HN | D boron | 0.59
D calcium 49 mg/l Ca HY276 HN | D calcium | 49
D hardness, total 51 mg/l Ca HY276 HN | D hardness, total | 51
D iron 28 ug/l Fe HY276 HN | D iron | 28
D magnesium 0.90 mg/l Mg HY276 HN | D magnesium | 0.90
D manganese 0.36 ug/l Mn HY276 HN | D manganese | 0.36
D potassium 2.1 mg/l K HY276 HN | D potassium | 2.1
D sodium 67 mg/l Na HY276 HN | D sodium | 67
D sulphate 1.0 mg/l SO4 HY276 HN | D sulphate | 1.0
D 1,2-dichloroethane <0.20 ug/l HY277 HN | D 1,2-dichloroethane | <0.20
D benzene <0.030 ug/l HY277 HN | D benzene | <0.030
D bromodichloromethane <0.68 ug/l HY277 HN | D bromodichloromethane | <0.68
D dibromochloromethane <0.64 ug/l HY277 HN | D dibromochloromethane | <0.64
D ethenes (total by calculation) 0.00 ug/l HY277 HN | D ethenes (total by calculation) | 0.00
D tetrachloroethene <0.16 ug/l HY277 HN | D tetrachloroethene | <0.16
D tetrachloromethane <0.11 ug/l HY277 HN | D tetrachloromethane | <0.11
D total THM 3.6 ug/l HY277 HN | D total THM | 3.6
D tribromomethane 3.6 ug/l HY277 HN | D tribromomethane | 3.6
D trichloroethene <0.13 ug/l HY277 HN | D trichloroethene | <0.13
D trichloromethane <0.78 ug/l HY277 HN | D trichloromethane | <0.78
D vinyl chloride <0.043 ug/l HY277 HN | D vinyl chloride | <0.043
D ammonium <0.020 mg/l NH4 HY-280 HN | D ammonium | <0.020
D chloride 150 mg/l Cl HY-280 HN | D chloride | 150
D nitrate <1.5 mg/l NO3 HY-280 HN | D nitrate | <1.5
D nitrite <0.0061 mg/l NO2 HY-280 HN | D nitrite | <0.0061
D phosphorus <76 ug/l P HY-280 HN | D phosphorus | <76
D bromate 10 ug BrO3/l HY-281 HN | D bromate | 10
# carbonate alkalinity 0.0 mg/l HCO3 HY-283 HN | # carbonate alkalinity | 0.0
# electrical conductivity 570 uS/cm 20C HY-283 HN | # electrical conductivity | 570
# fluoride <0.038 mg/l F HY-283 HN | # fluoride | <0.038
# hydrogen ion (pH) 8.1 pH units HY-283 HN | # hydrogen ion (pH) | 8.1
# total alkalinity 66 mg/l HCO3 HY-283 HN | # total alkalinity | 66
* pesticides total (calculated) 0.00 ug/l In House HN | * pesticides total (calculated) | 0.00
* 1,2-dibromo-3-chloropropane <1.0 ug/l O102 HN | * 1,2-dibromo-3-chloropropane | <1.0
* 1,2-dibromoethane <1.0 ug/l O102 HN | * 1,2-dibromoethane | <1.0
D 3:3 FTCA <0.009 ug/l Sub-Contracted SU | D 3:3 FTCA | <0.009
D 4:2 FTSA <0.004 ug/l Sub-Contracted SU | D 4:2 FTSA | <0.004
D 5:3 FTCA <0.005 ug/l Sub-Contracted SU | D 5:3 FTCA | <0.005
D 6:2 Cl-PFESA <0.002 ug/l Sub-Contracted SU | D 6:2 Cl-PFESA | <0.002
D 6:2 FTSA <0.005 ug/l Sub-Contracted SU | D 6:2 FTSA | <0.005
D 7:3 FTCA <0.007 ug/l Sub-Contracted SU | D 7:3 FTCA | <0.007
D 8:2 Cl-PFESA <0.004 ug/l Sub-Contracted SU | D 8:2 Cl-PFESA | <0.004
D 8:2 FTSA <0.004 ug/l Sub-Contracted SU | D 8:2 FTSA | <0.004
D DONA <0.003 ug/l Sub-Contracted SU | D DONA | <0.003
* epichlorohydrin (subcontracted) <0.10 ug/l Sub-Contracted SU | * epichlorohydrin (subcontracted) | <0.10
D EtFOSA <0.005 ug/l Sub-Contracted SU | D EtFOSA | <0.005
D EtFOSE <0.003 ug/l Sub-Contracted SU | D EtFOSE | <0.003
D FBSA <0.005 ug/l Sub-Contracted SU | D FBSA | <0.005
D FHxSA <0.003 ug/l Sub-Contracted SU | D FHxSA | <0.003
D FOSA <0.004 ug/l Sub-Contracted SU | D FOSA | <0.004
D HFPO-DA <0.008 ug/l Sub-Contracted SU | D HFPO-DA | <0.008
D HFPO-TA <0.004 ug/l Sub-Contracted SU | D HFPO-TA | <0.004
D MeFOSA <0.007 ug/l Sub-Contracted SU | D MeFOSA | <0.007
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?
| #NAME? | #NAME?